## Manual
Pennsylvania Act 129 Lighting Audit and Design Tool
MANUAL
Table of Contents:
I. Purpose
II. Organization
III. User Guide
IV. Notes
V. Disclaimer
I. Purpose
The purpose of the Lighting Audit and Design Tool is two-fold:
1. To document the pre- and post-installation case.
2. To facilitate the calculation of energy savings and demand reduction for large lighting installations.
II. Organization
The Lighting Audit and Design Tool is organized into 9 sheets.
(1) Manual
The "Manual" sheet contains the manual for using the Lighting Audit and Design Tool.
(2) Changelog
The "Changelog" sheet provides a brief description of major changes from the previous version.
(3) Glossary
The "Glossary" sheet is a reference defining key terms and column headings for the "Lighting Form" sheet.
(4) Lighting Form
The "Lighting Form" sheet is the main worksheet that calculates energy savings and peak demand reduction, following the conventions and equations described in the PA TRM. All key variables are entered on this sheet.
(5) User Input
The "User Input" sheet contains tables that allow additional customization of the "Lighting Form" for specific cases. These tables provide the following capabilities:
Table 1: Defining "Hours of Use" and "Coincidence Factor" for the "Other" facility type. This table is required when "Other" is selected in Cell J2 of the "Lighting Form" tab. Table 2: Defining "Hours of Use" and "Coincidence Factor" for each usage group. This table is to be used when groups of fixtures operate under different schedules for a single project. Table 3: Defining "Control Factor" for Lighting Controls. This table allows the use of custom control factors for lighting control technologies not listed in this tool. Table 4: Defining a fixture wattage according to specification sheets. This table is required when (1) a fixture is not listed in the Wattage Table, or (2) the manufacturer's cut sheet indicates that the difference in delta-watts of fixture wattages (i.e. difference in delta watts of baseline and actual efficient fixture wattage and delta watts of baseline and nearest matching appendix C efficient fixture) is more than 10%.
(6) Wattage Table
The "Wattage Table" sheet contains the master list of fixtures recognized by the Lighting Audit and Design Tool. The original source data is the NYSERDA Standard Wattage Table. Each fixture listed has a unique fixture code, description, and stipulated wattage value. Inclusion of a fixture in this table does not guarantee compliance with specific program requirements.
(7) Fixture Code Legend
The "Fixture Code Legend" sheet contains a legend explaining how fixture codes are constructed and how to read and identify fixture codes.
(8) Fixture Code Locator
The "Fixture Code Locator" sheet contains a tool to assist users locate a specific code on the Wattage Tables by specifying key lighting parameters. Fill in the tan fields by selecting from the pull down menu. Some fixtures in the Wattage Table may not be able to be located with this tool.
(9) Prescriptive Table
The "Prescriptive Table" sheet contains a list of fixtures that qualify under a prescriptive path. Only participants who (1) have savings under 20 kW and (2) self-certify the baseline fixtures may use the prescriptive table to the extent that actual existing fixtures match the assumed baseline fixtures in the prescriptive table. Customers using the Prescriptive Method must be categorized by building type to determine HOU and CF. If the exact building type is not listed, select the closest building type available. The "other" category is not allowed for the Prescriptive Method.
III. User Guide
1. This tool is required for projects over 20 kW of connected load savings to facilitate calculation of savings pursuant to the PA TRM. Use of this tool for projects under 20 kW should conform to EDC program rules. Consult the TRM for clarification on rules for calculating savings. 2. Begin at the "Lighting Form" sheet. Complete cells C2, C3, and C4 in the top section of the worksheet to identify the project. Select the appropriate facility type from the drop down list. The corresponding Hours of Use (HOU) and Coincidence Factor (CF) values from the PA Technical Reference Manual (TRM) will be automatically loaded. These HOU and CF values will be applied to all fixtures unless the following conditions apply:
A) If the facility type cannot be found in the drop down list, select "Other". On the "User Input" sheet, complete Table 1 by defining HOU and CF for the project according to the user's best judgment and best knowledge available (e.g. facility interviews, posted schedules, or metered data). Unreasonable values are subject to adjustment by evaluators. B) If determined that groups of lighting fixtures have different operating schedules, usage groups are strongly recommended. In Table 2 of the "User Input" sheet, set up usage groups by defining HOU and CF for each usage group. HOU values must be derived from facility interviews, posted hours, or metered data. After setup is complete for all usage groups, the appropriate usage group can be selected for each line item in Column E of the "Lighting Form" sheet.
3. On the "Lighting Form" sheet, complete the tan sections for each line item. Each line item represents fixtures in a discrete area sharing a common baseline fixture, retrofit fixture, controls type, hours, coincidence factor and space cooling type. Fixtures with different entries for any of these categories must be on separate lines. Each line entry must be definitive enough to allow verification of fixture counts in well delineated and discrete areas. Please note the following condition:
A) If third-party lighting inventory forms are provided and complete, a single line item on Appendix C can represent multiple areas provided that the baseline fixture, retrofit fixture, controls type, hours, coincidence factor, and space cooling type entries for the combined line items are identical. The completed third-party lighting inventory forms will be used to identify fixtures in discrete areas.
4. Complete Columns B, C, and D to identify each line item. The combination of these three fields should be unique to each line item to facilitate verification processes.
5. For Column E, select the appropriate usage group. See step 2 above for additional guidance. If usage groups are not required, select N/A.
6. For Column G, select the appropriate type of cooling for the space represented by the line item (i.e. where the fixtures are being installed). The categories include:
a) COOL - Air conditioned or cooled space b) FREZ - Freezer space c) MTRF - Medium-temperature refrigerated space d) HTRF - High-temperature refrigerated space e) UNCL - Uncooled space
7. Input the quantity of fixtures in Columns H and M and fixture codes in Columns I and N. Each fixture must be identified by a fixture code, which determines the wattage as defined by the Wattage Tables in the "Wattage Table" sheet. Codes are constructed using the legend in the "Fixture Code Legend" sheet. Users may manually search for the fixture code in the Wattage Table. Users requiring assistance identifying codes may use the tool provided in the "Fixture Code Locator" sheet. Please note the following conditions:
A) If a fixture code is not listed in the Wattage Table, a manufacturer's cut sheet (specification sheet) must be provided to determine the wattage of the associated fixture. Select the "User Input" sheet and fill out the "Description" and "Watts/Fixture" categories for cut sheets submitted. Wattage must be easily identifiable on the cut sheet. On the "Lighting Form" sheet, fixture codes "Cut Sheet #" can now be used. B) If the manufacturer's cut sheet indicates that the difference in delta-watts of fixture wattages (i.e. difference in delta watts of baseline and actual efficient fixture wattage and delta watts of baseline and nearest matching appendix C efficient fixture) is more than 10%, the cut sheet value may be used. Select the "User Input" sheet and fill out the "Description" and "Watts/Fixture" categories for cut sheets submitted. Wattage must be easily identifiable on the cut sheet. On the "Lighting Form" sheet, fixture codes "Cut Sheet #" can now be used.
8. Select the appropriate controls technology for the fixtures in Columns L and Q. Controls supported by this tool include:
1) S_LS - Light Switch for Switch Strategy;
2) O_OS - Occupancy Sensors for Occupancy Strategy;
3) O_TC - Time Clocks for Occupancy Strategy;
4) O_EMS - Energy Management System for Occupancy Strategy;
5) DL_PS - Photosensors for Daylighting Strategy;
6) DL_TC - Time Clocks for Daylighting Strategy;
7) PT_DIM - Dimmers for Personal Tuning Strategy;
8) PT_WS - Wireless on-off switches for Personal Tuning Strategy;
9) PT_BLS - Bi-level switches for Personal Tuning Strategy;
10) PT_CC - Computer based controls for Personal Tuning Strategy;
11) PT_PSS - Pre-set scene selection for Personal Tuning Strategy;
12) IT_DIM - Dimmable ballasts for Institutional Tuning Strategy;
13) IT_DIM - On-off or dimmer switches for Institutional Tuning Strategy;
14) MT - Multiple Types (Occupancy and personal; tuning/daylighting and other combinations)
A) If only controls are installed and fixtures are not changed, the fixture codes in the pre-installation case and the post-installation case should match. The tool can appropriately calculate savings for a controls-only improvement.
9. Repeat steps 3 to 8 to complete each line. For further clarification on a specific field or column, please see the "Glossary" sheet. If additional assistance is required, please contact the program manager.
IV. General Note
It is worth noting that magnetic ballasts cannot be manufactured after July 1, 2010 based on the Energy Policy and Conservation Act of 2000. This makes assumptions as to future savings and the Total Resource Cost of the retrofit unclear.
V. Disclaimer
This tool allows for custom entries for several fields. This document does not modify any requirements of the PA TRM. If any discrepancy between the TRM and this document exist, the TRM should be followed.

## Changelog
Pennsylvania Act 129 Lighting Audit and Design Tool
CHANGELOG
Version 12 (Effective June 3, 2010)
1) | Released with TRM Order in June 2010
Version 13 (Submitted October 27, 2010. Effective June 1, 2011)
1) | Created Changelog
2) | Revised "Manual" and "Glossary" to improve user guide and increase usability
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM
4) | Added Stipulated Usage Group EFLH Table in the "User Input" sheet
5) | Added new building types with corresponding EFLH and CF values
6) | Combined "Wattage Table" and "Extension Table" into one sheet (see column I of the Wattage Table)
7) | Revised fixtures codes and descriptions in Standard Wattage Table
8) | Renamed "Fixture Code Generator" to "Fixture Code Locator" and corrected some programming glitches
Version 14 (Submitted January 19, 2011. Effective June 1, 2011)
1) | In "Manual", section 7.B, the threshold was corrected to 10%, not 15%
2) | In "User Input", Table 5 was revised to reflect TRM Table 3-2
3) | In "User Input", added note to list source for Tables 3 and 5
4) | In "Glossary", added definitions for "pre-installation" and "post-installation"
5) | In "Lighting Form", the EFLH table was updated to reflect TRM Table 3-5
Version 15 (Submitted September 13, 2011 for 2012 Tentative Order)
1) | Global change, replaced all instances of EFLH with HOU
2) | In "User Input", removed old Table 5 to eliminate stipulated hours for usage groups.
3) | In "User Input", added Table 3 to allow custom SVG factor input
Version 16 (Submitted December 4, 2011 for 2012 Final Order)
1) | In "Manual", updated language regarding usage groups.
2) | In "Glossary", removed all references to the old 50 kW threshold.
3) | In "Lighting Form", updated the HOU table to reflect the 2012 TRM (Table 3-4).
4) | In "User Input", added column for custom CF for each usage group.
Version 17 (Submitted August 31, 2012 for 2013 Tentative Order)
1) In "Lighting Form", updated HOU and CF values lookup table to reflect the 2013 TRM table.
2) In "Lighting Form", added new building types with corresponding EFLH and CF values to reflect the 2013 TRM table.
3) In "Lighting Form", updated Control Technologies and Savings Factors values lookup table to reflect 2013 TRM table.
4) Revised "Manual" and "Glossary" to reflect new changes to the 2013 TRM
Version 18 (Submitted December 3, 2012 for 2013 Final Order)
1) Revised "Manual" to reflect new changes to the 2013 TRM

## Glossary
Pennsylvania Act 129 Lighting Audit and Design Tool
GLOSSARY
Project Identification
Cell C2: | "Applicant Name" is the applicant name.
Cell C3: | "Facility Name" is the facility name.
Cell C4: | "Installation Date" is the completion date of all lighting equipment.
Cell J2: | "Facility Type" is the primary function of the facility. The categories are based on the PA TRM. "Other" should be used when no other category is sufficient. If a project consists of multiple facility types, it is recommended to utilize usage groups to improve savings estimates (See Column E).
General Definition
Cell H7: | "Pre-Installation" refers to the baseline condition, or the existing condition of the facility prior to the implementation of the energy conservation measure. This definition assumed throughout Appendix C.
Cell M7: | "Post-Installation" refers to the retrofit condition, or the condition of the facility after the implementation of the energy conservation measure. This definition assumed throughout Appendix C.
Line Item Identification
Column A: | "Line Item" is to index fixtures. For identification purposes.
Column B: | "Building Address" is the address of the facility where the fixtures are being installed. For identification purposes.
Column C: | "Floor" is the floor on which the fixtures are being installed. For identification purposes.
Column D: | "Area Description" is a short description of the specific area in the building where the fixtures are being installed. For identification purposes.
Column E: | "Usage Group" is an area that exhibits the same usage characteristics. Some projects may contain areas with different operating hours (e.g. lobby, office, dining area, conference room). Usage groups improve precision and accuracy of lighting savings by assigning HOU for each distinct area because a single HOU value may not properly represent the facility. For further assistance on using usage groups, see the "Manual" sheet.
Column F: | "Hours of Use", or "HOU", is the average annual operating hours of the baseline lighting fixture without controls.
Column G: | "Space Cooling Type" is the type of cooling that is used for the space in which the fixtures are being installed. This field determines the value of the interactive factors for energy and demand (see Column T and U for definitions). The form allows for the following cooling types: Air conditioned or cooled space; Freezer space; Medium-temperature refrigerated space; High-temperature refrigerated space; Uncooled space.
Fixture Information
Column H: | "Pre Fixture No." is the number of fixtures in the pre-installation case.
Column I: | "Pre Fixture Code" is the type of fixture in the pre-installation case. The code is selected from the "Wattage Table" sheet. If the code is unknown, the Fixture Code Locator can assist users find the correct code by filling out key parameters. If the code is not listed in the "Wattage Table" sheet, a cut sheet must be provided to determine the wattage of the associated fixture. To use cut sheets for determining wattage, "cut sheet" codes must first be defined in the "User Input" sheet. For further assistance on setting up cut sheet wattages for use in the lighting form, see Section II.2.C in the "Manual" sheet.
Column J: | "Pre Watts/Fixture" is the watts per fixture for the pre-installation case. This field is populated automatically, based on the fixture code entered in Column I.
Column K: | "Pre Watts/Space" represents the total watts in the designated space for the pre-installation case.
Column L: | "Pre Control" is the control technology in the pre-installation case. The form allows for the following controls technologies: Light Switch for Switch Strategy; Occupancy Sensors, Time Clocks and Energy Management System for Occupancy Strategy; Photosensors and Time Clocks for Daylighting Strategy; Dimmers, Wireless on-off switches, Bi-level switches, Computer based controls, and Pre-set scene selection for Personal Tuning Strategy; Dimmable ballasts and On-off or dimmer switches for Institutional Tuning Strategy; Multiple Types (Occupancy and personal tuning/daylighting and other combinations).
Column M: | "Post Fixture No." is the number of fixtures in the post-installation case.
Column N: | "Post Fixture Code" is the type of fixture in the post-installation case. The code is selected from the "Wattage Table" sheet. If the code is unknown, the Fixture Code Locator can assist users find the correct code by filling out key parameters. If the code is not listed in the "Wattage Table" sheet, a cut sheet must be provided to determine the wattage of the associated fixture. To use cut sheets for determining wattage, "cut sheet" codes must first be defined in the "User Input" sheet. For further assistance on setting up cut sheet wattages for use in the lighting form, see Section II.2.C in the "Manual" sheet.
Column O: | "Post Watts/Fixture" is the watts per fixture for the post-installation case. This field is populated automatically, based on the fixture code entered in Column N.
Column P: | "Post Watts/Space" represents the total watts in the designated space for the post-installation case.
Column Q: | "Post Control" is the control technology in the post-installation case.The form allows for the following controls technologies: Light Switch for Switch Strategy; Occupancy Sensors, Time Clocks and Energy Management System for Occupancy Strategy; Photosensors and Time Clocks for Daylighting Strategy; Dimmers, Wireless on-off switches, Bi-level switches, Computer based controls, and Pre-set scene selection for Personal Tuning Strategy; Dimmable ballasts and On-off or dimmer switches for Institutional Tuning Strategy; Multiple Types (Occupancy and personal tuning/daylighting and other combinations).
Output Information
Column R: | "Change in Connected Load" is the difference in installed watts between the pre-installation and post-installation cases. This does not take into account coincidence factors, controls, or interactive factors.
Column S: | "Coincidence Factor", or "CF", is the percentage of the total lighting connected load that is on during electric system’s peak period, defined as the top 100 hours.
Column T: | "Interactive Factor Demand" is the secondary demand reduction from cooling savings resulting from a decrease in heat generated by lighting. This applies to lighting in space that has air conditioning or refrigeration only. This factor is determined by Column G.
Column U: | "Interactive Factor Energy" is the secondary energy savings from cooling savings resulting from a decrease in heat generated by lighting. This applies to lighting in space that has air conditioning or refrigeration only. This factor is determined by Column G.
Column V: | "Controls Factor", or "SVG", is the percent of time that lights are off due to lighting controls relative to a manual light switch. This factor is determined by Column Q.
Column W: | "Peak Demand Savings" is the peak demand reduced taking into account coincidence factors, controls, and interactive factors, calculated using TRM protocols.
Column X: | "Annual kWh Saved" is the total annual energy saved by the lighting improvement.

## Lighting Form
Lighting Form |  | Appendix C of the PA TRM |  |  |  | For instructions, see the Users Guide in the "Manual" sheet.
Applicant Name: | [5 empty] | Facility Type:
Facility Name: | [5 empty] | Default Hours of Use (HOU):
Installation Date: | [5 empty] | Default Coincidence Factor (CF):
| Input Field |  | Computed Field
[7 empty] | PRE-INSTALLATION (BASELINE) |  |  |  |  | POST-INSTALLATION (RETROFIT)
Line Item | Building Address | Floor | Area Description | Usage Group | Hours of Use (HOU) | Space Cooling Type | Pre Fixture No. | Pre Fixture Code | Pre Watts / Fixture | Pre kW / Space | Pre Control | Post Fixture No. | Post Fixture Code | Post Watts / Fixture | Post kW / Space | Post Control | Change in Connected Load | Coincidence Factor | Interactive Factor (demand) | Interactive Factor (energy) | Controls Factor | Peak Demand Savings | Annual kWh Saved | LOOKUP TABLES
Ex. | 200 First Avenue | 1 | Office | N/A | 2567 | COOL | 3 | F44ILL | 112 | 0.336 | S_LS | 3 | F42ILL | 59 | 0.177 | O_OS | 0.159 | 61% | 34% | 12% | 24% | 0.12997 | 579.2631 | Facility Type | HOU | CF | Usage Group Name | HOU | CF | Space Type | Abbrv. | IF_Demand | IF_Energy
[24 empty] | Auto Related | 4056 | 0.62 | N/A |  |  | Air Conditioned/Cooled space | COOL | 0.34 | 0.12 | Strategy | Definition | Control Type | Abbrv. | SVG
1 | [23 empty] | Daycare | 2590 | 0.62 | Usage Group 1 | Edit | Edit | Freezer space | FREZ | 0.5 | 0.5 | Switch | Manual On/Off Switch | Light Switch | S_LS | 0%
2 | [23 empty] | Dusk-to-Dawn / Exterior Lighting | 3833 | 0 | Usage Group 2 | Edit | Edit | Medium-temperature refrigerated space | MTRF | 0.29 | 0.29 | Occupancy | Adjusting light levels according to the presence of occupants | Occupancy Sensors | O_OS | 24%
3 | [23 empty] | Education – School | 1632 | 0.31 | Usage Group 3 | Edit | Edit | High-temperature refrigerated space | HTRF | 0.18 | 0.18 |  |  | Time Clocks | O_TC | 24%
4 | [23 empty] | Education – College/University | 2348 | 0.76 | Usage Group 4 | Edit | Edit | Uncooled space | UNCL | 0 | 0 |  |  | Energy Management System | O_EMS | 24%
5 | [23 empty] | Grocery | 4660 | 0.87 | Usage Group 5 | Edit | Edit |  |  |  |  | Daylighting | Adjusting light levels automatically in response to the presence of natural light | Photosensors | DL_PS | 28%
6 | [23 empty] | Health/Medical – Clinic | 3213 | 0.73 | Usage Group 6 | Edit | Edit | [6 empty] | Time Clocks | DL_TC | 28%
7 | [23 empty] | Hospitals | 5182 | 0.8 | Usage Group 7 | Edit | Edit |  |  |  |  | Personal Tuning | Adjusting individual light levels by occupants according to their personal preferences; applies, for example, to private offices, workstation-specific lighting in open-plan offices, and classrooms | Dimmers | PT_DIM | 31%
8 | [23 empty] | Industrial Manufacturing – 1 Shift | 2857 | 0.57 | Usage Group 8 | Edit | Edit | [6 empty] | Wireless on-off switches | PT_WS | 31%
9 | [23 empty] | Industrial Manufacturing – 2 Shift | 4730 | 0.57 | Usage Group 9 | Edit | Edit | [6 empty] | Bi-level switches | PT_BLS | 31%
10 | [23 empty] | Industrial Manufacturing – 3 Shift | 6631 | 0.57 | Usage Group 10 | Edit | Edit | [6 empty] | Computer based controls | PT_CC | 31%
11 | [23 empty] | Libraries | 2566 | 0.62 | [9 empty] | Pre-set scene selection | PT_PSS | 31%
12 | [23 empty] | Lodging – Guest Rooms | 914 | 0.09 | [7 empty] | Institutional Tuning | Adjustment of light levels through commissioning and technology to meet location specific needs or building policies; or provision of switches or controls for areas or groups of occupants; examples of the former include high-end trim dimming (also known as ballast tuning or reduction of ballast factor), task tuning and lumen maintenance | Dimmable ballasts | IT_DIM | 36%
13 | [23 empty] | Lodging – Common Spaces | 7884 | 0.9 | [9 empty] | On-off or dimmer switches for non-personal tuning | IT_DIM | 36%
14 | [23 empty] | Multi-Family (Common Areas) - High-rise & Low-rise | 5950 | 0.62 | [7 empty] | Multiple Types | Includes combination of any of the types described above. Occupancy and personal tuning, daylighting and occupancy are most common. | Occupancy and personal tuning/daylighting and occupancy | MT | 38%
15 | [23 empty] | Nursing Home | 4160 | 0.62 | [7 empty] | Other | Other control technologies not listed above | Control Type 1 | CT1 | Edit
16 | [23 empty] | Office | 2567 | 0.61 | [9 empty] | Control Type 2 | CT2 | Edit
17 | [23 empty] | Parking Garages | 6552 | 0.62 | [9 empty] | Control Type 3 | CT3 | Edit
18 | [23 empty] | Public Order and Safety | 5366 | 0.62 | [9 empty] | Control Type 4 | CT4 | Edit
19 | [23 empty] | Public Assembly (one shift) | 2610 | 0.62 | [9 empty] | Control Type 5 | CT5 | Edit
20 | [23 empty] | Public Services (nonfood) | 3425 | 0.62
21 | [23 empty] | Restaurant | 3613 | 0.65
22 | [23 empty] | Retail | 2829 | 0.73
23 | [23 empty] | Religious Worship/Church | 1810 | 0.62
24 | [23 empty] | Storage Conditioned/Unconditioned | 3420 | 0.62
25 | [23 empty] | Warehouse | 2316 | 0.54
26 | [23 empty] | 24/7 Facilities or Spaces | 8760 | 1
27 | [23 empty] | Other (Fill in "User Input" sheet) | Edit | Edit
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
Totals
Note on G8: Space Cooling Type Select the type of cooling in the space where the fixtures are being installed from the pull down menu. COOL - Air Conditioned or cooled space FREZ - Freezer space MTRF - Medium-temperature refrigerated space HTRF - High-temperature refrigerated space UNCL - Uncooled space
Note on L8: Existing Control Select the lighting control method from the pull down menu. S_LS - Light Switch for Switch Strategy; O_OS - Occupancy Sensors for Occupancy Strategy; O_TC - Time Clocks for Occupancy Strategy; O_EMS - Energy Management System for Occupancy Strategy; DL_PS - Photosensors for Daylighting Strategy; DL_TC - Time Clocks for Daylighting Strategy; PT_DIM - Dimmers for Personal Tuning Strategy; PT_WS - Wireless on-off switches for Personal Tuning Strategy; PT_BLS - Bi-level switches for Personal Tuning Strategy; PT_CC - Computer based controls for Personal Tuning Strategy; PT_PSS - Pre-set scene selection for Personal Tuning Strategy; IT_DIM - Dimmable ballasts for Institutional Tuning Strategy; IT_DIM - On-off or dimmer switches for Institutional Tuning Strategy; MT - Multiple Types (Occupancy and personal ;tuning/daylighting and other combinations) If no category is sufficient, select "CT1" and input SVG value in Table 3 of the "User Input" sheet.
Note on J2: Facility Type Select the facility type that best describes your facility. If no category is sufficiently describes your facility, select "Other" and input EFLH and CF values in Table 1 of the "User Input" sheet.
Note on Q8: Existing Control Select the lighting control method from the pull down menu. S_LS - Light Switch for Switch Strategy; O_OS - Occupancy Sensors for Occupancy Strategy; O_TC - Time Clocks for Occupancy Strategy; O_EMS - Energy Management System for Occupancy Strategy; DL_PS - Photosensors for Daylighting Strategy; DL_TC - Time Clocks for Daylighting Strategy; PT_DIM - Dimmers for Personal Tuning Strategy; PT_WS - Wireless on-off switches for Personal Tuning Strategy; PT_BLS - Bi-level switches for Personal Tuning Strategy; PT_CC - Computer based controls for Personal Tuning Strategy; PT_PSS - Pre-set scene selection for Personal Tuning Strategy; IT_DIM - Dimmable ballasts for Institutional Tuning Strategy; IT_DIM - On-off or dimmer switches for Institutional Tuning Strategy; MT - Multiple Types (Occupancy and personal ;tuning/daylighting and other combinations) If no category is sufficient, select "CT1" and input SVG value in Table 3 of the "User Input" sheet.

## User Input
Table 1 - Defining HOU and CF for "Other" Facility Type |  |  | Table 4 - Defining Wattages for Fixtures not in the Wattage Table or Exceptional Cases
Facility Type | HOU | CF | Fixture Code | Description | Watts/Fixture
Other | Edit | Edit | Cut Sheet 1 | Edit | Edit
|  |  | Cut Sheet 2 | Edit | Edit
Table 2 - Defining HOU for Usage Groups |  |  | Cut Sheet 3 | Edit | Edit
Usage Group Name | HOU | CF | Cut Sheet 4 | Edit | Edit
Usage Group 1 | Edit | Edit | Cut Sheet 5 | Edit | Edit
Usage Group 2 | Edit | Edit | Cut Sheet 6 | Edit | Edit
Usage Group 3 | Edit | Edit | Cut Sheet 7 | Edit | Edit
Usage Group 4 | Edit | Edit | Cut Sheet 8 | Edit | Edit
Usage Group 5 | Edit | Edit | Cut Sheet 9 | Edit | Edit
Usage Group 6 | Edit | Edit | Cut Sheet 10 | Edit | Edit
Usage Group 7 | Edit | Edit | Cut Sheet 11 | Edit | Edit
Usage Group 8 | Edit | Edit | Cut Sheet 12 | Edit | Edit
Usage Group 9 | Edit | Edit | Cut Sheet 13 | Edit | Edit
Usage Group 10 | Edit | Edit | Cut Sheet 14 | Edit | Edit
|  |  | Cut Sheet 15 | Edit | Edit
Table 3 - Defining Control Factor for Lighting Controls |  |  | Cut Sheet 16 | Edit | Edit
Control Type Name | Abbrv. | SVG | Cut Sheet 17 | Edit | Edit
Control Type 1 | CT1 | Edit | Cut Sheet 18 | Edit | Edit
Control Type 2 | CT2 | Edit | Cut Sheet 19 | Edit | Edit
Control Type 3 | CT3 | Edit | Cut Sheet 20 | Edit | Edit
Control Type 4 | CT4 | Edit | Cut Sheet 21 | Edit | Edit
Control Type 5 | CT5 | Edit | Cut Sheet 22 | Edit | Edit
|  |  | Cut Sheet 23 | Edit | Edit
Note: |  |  | Cut Sheet 24 | Edit | Edit
1. Complete tables only as required by the User's Guide. |  |  | Cut Sheet 25 | Edit | Edit
|  |  | Cut Sheet 26 | Edit | Edit
|  |  | Cut Sheet 27 | Edit | Edit
|  |  | Cut Sheet 28 | Edit | Edit
|  |  | Cut Sheet 29 | Edit | Edit
|  |  | Cut Sheet 30 | Edit | Edit
|  |  | Cut Sheet 31 | Edit | Edit
|  |  | Cut Sheet 32 | Edit | Edit
|  |  | Cut Sheet 33 | Edit | Edit
|  |  | Cut Sheet 34 | Edit | Edit
|  |  | Cut Sheet 35 | Edit | Edit
|  |  | Cut Sheet 36 | Edit | Edit
|  |  | Cut Sheet 37 | Edit | Edit
|  |  | Cut Sheet 38 | Edit | Edit
|  |  | Cut Sheet 39 | Edit | Edit
|  |  | Cut Sheet 40 | Edit | Edit
|  |  | Cut Sheet 41 | Edit | Edit
|  |  | Cut Sheet 42 | Edit | Edit
|  |  | Cut Sheet 43 | Edit | Edit
|  |  | Cut Sheet 44 | Edit | Edit
|  |  | Cut Sheet 45 | Edit | Edit
|  |  | Cut Sheet 46 | Edit | Edit
|  |  | Cut Sheet 47 | Edit | Edit
|  |  | Cut Sheet 48 | Edit | Edit
|  |  | Cut Sheet 49 | Edit | Edit
|  |  | Cut Sheet 50 | Edit | Edit

## Wattage Table
Pennsylvania Act 129 Lighting Audit and Design Tool
WATTAGE TABLE
FIXTURE CODE | LAMP CODE | DESCRIPTION | BALLAST | LAMP / FIXT | WATT / LAMP | WATT / FIXT | DATE OF REVISION | DESCRIPTION OF REVISION
Compact Fluorescent Light Fixtures
CF10/2D | CFD10W | Compact Fluorescent, 2D, (1) 10W lamp | Mag-STD | 1 | 10 | 16
CF10/2D-L | CFD10W | Compact Fluorescent, 2D, (1) 10W lamp | Electronic | 1 | 10 | 12
CF11/1 | CF11W | Compact Fluorescent, (1) 11W lamp | Mag-STD | 1 | 11 | 13
CF11/2 | CF11W | Compact Fluorescent, (2) 11W lamp | Mag-STD | 2 | 11 | 26
CF16/2D | CFD16W | Compact Fluorescent, 2D, (1) 16W lamp | Mag-STD | 1 | 16 | 26
CF16/2D-L | CFD16W | Compact Fluorescent, 2D, (1) 16W lamp | Electronic | 1 | 16 | 18
CF18/3-L | CF18W | Compact Fluorescent, (3) 18W lamp | Electronic | 3 | 18 | 60
CF21/2D | CFD21W | Compact Fluorescent, 2D, (1) 21W lamp | Mag-STD | 1 | 21 | 26
CF21/2D-L | CFD21W | Compact Fluorescent, 2D, (1) 21W lamp | Electronic | 1 | 21 | 22
CF23/1 | CF23W | Compact Fluorescent, (1) 23W lamp | Mag-STD | 1 | 23 | 29
CF23/1-L | CF23W | Compact Fluorescent, (1) 23W lamp | Electronic | 1 | 23 | 25
CF26/3-L | CF26W | Compact Fluorescent, (3) 26W lamp | Electronic | 3 | 26 | 82
CF26/4-L | CF26W | Compact Fluorescent, (4) 26W lamp | Electronic | 4 | 26 | 108
CF26/6-L | CF26W | Compact Fluorescent, (6) 26W lamp | Electronic | 6 | 26 | 162
CF26/8-L | CF26W | Compact Fluorescent, (8) 26W lamp | Electronic | 8 | 26 | 216
CF28/2D | CFD28W | Compact Fluorescent, 2D, (1) 28W lamp | Mag-STD | 1 | 28 | 35
CF28/2D-L | CFD28W | Compact Fluorescent, 2D, (1) 28W lamp | Electronic | 1 | 28 | 28
CF32/3-L | CF32W | Compact Fluorescent, (3) 32W lamp | Electronic | 3 | 32 | 114
CF32/4-L | CF32W | Compact Fluorescent, (4) 32W lamp | Electronic | 4 | 32 | 152
CF32/6-L | CF32W | Compact Fluorescent, (6) 32W lamp | Electronic | 6 | 32 | 228
CF32/8-L | CF32W | Compact Fluorescent, (8) 32W lamp | Electronic | 8 | 32 | 304
CF38/2D | CFD38W | Compact Fluorescent, 2D, (1) 38W lamp | Mag-STD | 1 | 38 | 46
CF38/2D-L | CFD38W | Compact Fluorescent, 2D, (1) 38W lamp | Electronic | 1 | 38 | 36
CF42/1-L | CF42W | Compact Fluorescent, (1) 42W lamp | Electronic | 1 | 42 | 48
CF42/2-L | CF42W | Compact Fluorescent, (2) 42W lamp | Electronic | 2 | 42 | 100
CF42/3-L | CF42W | Compact Fluorescent, (3) 42W lamp | Electronic | 3 | 42 | 141
CF42/4-L | CF42W | Compact Fluorescent, (4) 42W lamp | Electronic | 4 | 42 | 188
CF42/6-L | CF42W | Compact Fluorescent, (6) 42W lamp | Electronic | 6 | 42 | 282
CF42/8-L | CF42W | Compact Fluorescent, (8) 42W lamp | Electronic | 8 | 42 | 376
CFQ10/1 | CFQ10W | Compact Fluorescent, quad, (1) 10W lamp | Mag-STD | 1 | 10 | 15
CFQ13/1 | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp | Mag-STD | 1 | 13 | 17
CFQ13/1-L | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp, BF=1.05 | Electronic | 1 | 13 | 15
CFQ13/2 | CFQ13W | Compact Fluorescent, quad, (2) 13W lamp | Mag-STD | 2 | 13 | 31
CFQ13/2-L | CFQ13W | Compact Fluorescent, quad, (2) 13W lamp, BF=1.0 | Electronic | 2 | 13 | 28
CFQ13/3 | CFQ13W | Compact Fluorescent, quad, (3) 13W lamp | Mag-STD | 3 | 13 | 48
CFQ15/1 | CFQ15W | Compact Fluorescent, quad, (1) 15W lamp | Mag-STD | 1 | 15 | 20
CFQ17/1 | CFQ17W | Compact Fluorescent, quad, (1) 17W lamp | Mag-STD | 1 | 17 | 24
CFQ17/2 | CFQ17W | Compact Fluorescent, quad, (2) 17W lamp | Mag-STD | 2 | 17 | 48
CFQ18/1 | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp | Mag-STD | 1 | 18 | 26
CFQ18/1-L | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp, BF=1.0 | Electronic | 1 | 18 | 20
CFQ18/2 | CFQ18W | Compact Fluorescent, quad, (2) 18W lamp | Mag-STD | 2 | 18 | 45
CFQ18/2-L | CFQ18W | Compact Fluorescent, quad, (2) 18W lamp, BF=1.0 | Electronic | 2 | 18 | 38
CFQ18/4 | CFQ18W | Compact Fluorescent, quad, (4) 18W lamp | Mag-STD | 4 | 18 | 90 | 2010-10-12 | Changed lamps/fixture from 2 to 4.
CFQ20/1 | CFQ20W | Compact Fluorescent, quad, (1) 20W lamp | Mag-STD | 1 | 20 | 23
CFQ20/2 | CFQ20W | Compact Fluorescent, quad, (2) 20W lamp | Mag-STD | 2 | 20 | 46
CFQ22/1 | CFQ22W | Compact Fluorescent, quad, (1) 22W lamp | Mag-STD | 1 | 22 | 24
CFQ22/2 | CFQ22W | Compact Fluorescent, quad, (2) 22W lamp | Mag-STD | 2 | 22 | 48
CFQ22/3 | CFQ22W | Compact Fluorescent, quad, (3) 22W lamp | Mag-STD | 3 | 22 | 72
CFQ25/1 | CFQ25W | Compact Fluorescent, quad, (1) 25W lamp | Mag-STD | 1 | 25 | 33
CFQ25/2 | CFQ25W | Compact Fluorescent, quad, (2) 25W lamp | Mag-STD | 2 | 25 | 66
CFQ26/1 | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp | Mag-STD | 1 | 26 | 33
CFQ26/1-L | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp, BF=0.95 | Electronic | 1 | 26 | 27
CFQ26/2 | CFQ26W | Compact Fluorescent, quad, (2) 26W lamp | Mag-STD | 2 | 26 | 66
CFQ26/2-L | CFQ26W | Compact Fluorescent, quad, (2) 26W lamp, BF=0.95 | Electronic | 2 | 26 | 50
CFQ26/3 | CFQ26W | Compact Fluorescent, quad, (3) 26W lamp | Mag-STD | 3 | 26 | 99
CFQ26/6-L | CFQ26W | Compact Fluorescent, quad, (6) 26W lamp, BF=0.95 | Electronic | 6 | 26 | 150
CFQ28/1 | CFQ28W | Compact Fluorescent, quad, (1) 28W lamp | Mag-STD | 1 | 28 | 33
CFQ9/1 | CFQ9W | Compact Fluorescent, quad, (1) 9W lamp | Mag-STD | 1 | 9 | 14
CFQ9/2 | CFQ9W | Compact Fluorescent, quad, (2) 9W lamp | Mag-STD | 2 | 9 | 23
CFS7/1 | CFS7W | Compact Fluorescent, spiral, (1) 7W lamp | Electronic | 1 | 7 | 7
CFS9/1 | CFS9W | Compact Fluorescent, spiral, (1) 9W lamp | Electronic | 1 | 9 | 9
CFS11/1 | CFS11W | Compact Fluorescent, spiral, (1) 11W lamp | Electronic | 1 | 11 | 11
CFS13/1 | CFS13W | Compact Fluorescent, spiral, (1) 13W lamp | Electronic | 1 | 13 | 13 | 2010-03-18 | New Code - From Energy Star
CFS15/1 | CFS15W | Compact Fluorescent, spiral, (1) 15W lamp | Electronic | 1 | 15 | 15
CFS20/1 | CFS20W | Compact Fluorescent, spiral, (1) 20W lamp | Electronic | 1 | 20 | 20
CFS23/1 | CFS23W | Compact Fluorescent, spiral, (1) 23W lamp | Electronic | 1 | 23 | 23
CFS26/1 | CFS26W | Compact Fluorescent, spiral, (1) 26W lamp | Electronic | 1 | 26 | 26 | 2010-03-18 | New Code - From Energy Star
CFS27/1 | CFS27W | Compact Fluorescent, spiral, (1) 27W lamp | Electronic | 1 | 27 | 27
CFT13/1 | CFT13W | Compact Fluorescent, twin, (1) 13W lamp | Mag-STD | 1 | 13 | 17
CFT13/2 | CFT13W | Compact Fluorescent, twin, (2) 13W lamp | Mag-STD | 2 | 13 | 31
CFT13/3 | CFT13W | Compact Fluorescent, twin, (3) 13 W lamp | Mag-STD | 3 | 13 | 48
CFT18/1 | CFT18W | Compact Fluorescent, long twin., (1) 18W lamp | Mag-STD | 1 | 18 | 24
CFT22/1 | CFT22W | Compact Fluorescent, twin, (1) 22W lamp | Mag-STD | 1 | 22 | 27
CFT22/2 | CFT22W | Compact Fluorescent, twin, (2) 22W lamp | Mag-STD | 2 | 22 | 54
CFT22/4 | CFT22W | Compact Fluorescent, twin, (4) 22W lamp | Mag-STD | 4 | 22 | 108
CFT24/1 | CFT24W | Compact Fluorescent, long twin, (1) 24W lamp | Mag-STD | 1 | 24 | 32
CFT28/1 | CFT28W | Compact Fluorescent, twin, (1) 28W lamp | Mag-STD | 1 | 28 | 33
CFT28/2 | CFT28W | Compact Fluorescent, twin, (2) 28W lamp | Mag-STD | 2 | 28 | 66
CFT32/1-L | CFM32W | Compact Fluorescent, twin or multi, (1) 32W lamp | Electronic | 1 | 32 | 34
CFT32/2-L | CFM32W | Compact Fluorescent, twin or multi, (2) 32W lamp | Electronic | 2 | 32 | 62
CFT32/6-L | CFM32W | Compact Fluorescent, twin or multi, (6) 32W lamp | Electronic | 6 | 32 | 186 | 2010-10-12 | Changed description from 2 to 6 lamps
CFT36/1 | CFT36W | Compact Fluorescent, long twin, (1) 36W lamp | Mag-STD | 1 | 36 | 51
CFT36/4-BX | CFT36W | Compact Fluorescent, Biax, (4) 36W lamp | Electronic | 4 | 36 | 148
CFT36/6-BX | CFT36W | Compact Fluorescent, Biax, (6) 36W lamp | Electronic | 6 | 36 | 212
CFT36/6-L | CFT36W | Compact Fluorescent, long Twin, (6) 36W lamp | Electronic | 6 | 36 | 198
CFT36/6-LH | CFT36W | Compact Fluorescent, long Twin, (6) 36W lamp/ High Ballast Factor | Electronic | 6 | 36 | 210 | 2010-10-12 | Changed fixture code from CFT36/6-L to CFT36/6-LH
CFT36/8-BX | CFT36W | Compact Fluorescent, Biax, (8) 36W lamp | Electronic | 8 | 36 | 296
CFT36/8-L | CFT36W | Compact Fluorescent, long Twin, (8) 36W lamp | Electronic | 8 | 36 | 270
CFT36/8-LH | CFT36W | Compact Fluorescent, long Twin, (8) 36W lamp/ High Ballast Factor | Electronic | 8 | 36 | 286 | 2010-10-12 | Changed fixture code from CFT36/8-L to CFT36/8-LH
CFT36/9-BX | CFT36W | Compact Fluorescent, Biax, (9) 36W lamp | Electronic | 9 | 36 | 318
CFT40/1 | CFT40W | Compact Fluorescent, twin, (1) 40W lamp | Mag-STD | 1 | 40 | 46
CFT40/12-BX | CFT40W | Compact Fluorescent, Biax, (12) 40W lamp | Electronic | 12 | 40 | 408
CFT40/1-BX | CFT40W | Compact Fluorescent, Biax, (1) 40W lamp | Electronic | 1 | 40 | 46
CFT40/1-L | CFT40W | Compact Fluorescent, long twin, (1) 40W lamp | Electronic | 1 | 40 | 43
CFT40/2 | CFT40W | Compact Fluorescent, twin, (2) 40W lamp | Mag-STD | 2 | 40 | 85
CFT40/2-BX | CFT40W | Compact Fluorescent, Biax, (2) 40W lamp | Electronic | 2 | 40 | 72
CFT40/2-L | CFT40W | Compact Fluorescent, long twin, (2) 40W lamp | Electronic | 2 | 40 | 72
CFT40/3 | CFT40W | Compact Fluorescent, twin, (3) 40 W lamp | Mag-STD | 3 | 40 | 133
CFT40/3-BX | CFT40W | Compact Fluorescent, Biax, (3) 40W lamp | Electronic | 3 | 40 | 102
CFT40/3-L | CFT40W | Compact Fluorescent, long twin, (3) 40W lamp | Electronic | 3 | 40 | 105
CFT40/4-BX | CFT40W | Compact Fluorescent, Biax, (4) 40W lamp | Electronic | 4 | 40 | 144
CFT40/5-BX | CFT40W | Compact Fluorescent, Biax, (5) 40W lamp | Electronic | 5 | 40 | 190
CFT40/6-BX | CFT40W | Compact Fluorescent, Biax, (6) 40W lamp | Electronic | 6 | 40 | 204
CFT40/6-L | CFT40W | Compact Fluorescent, long Twin, (6) 40W lamp | Electronic | 6 | 40 | 220
CFT40/6-LH | CFT40W | Compact Fluorescent, long Twin, (6) 40W lamp/ High Ballast Factor | Electronic | 6 | 40 | 233 | 2010-10-12 | Changed fixture code from CFT40/6-L to CFT40/6-LH
CFT40/8-BX | CFT40W | Compact Fluorescent, Biax, (8) 40W lamp | Electronic | 8 | 40 | 288
CFT40/8-L | CFT40W | Compact Fluorescent, long Twin, (8) 40W lamp | Electronic | 8 | 40 | 300
CFT40/8-LH | CFT40W | Compact Fluorescent, long Twin, (8) 40W lamp/ High Ballast Factor | Electronic | 8 | 40 | 340 | 2010-10-12 | Changed fixture code from CFT40/8-L to CFT40/8-LH
CFT40/9-BX | CFT40W | Compact Fluorescent, Biax, (9) 40W lamp | Electronic | 9 | 40 | 306
CFT5/1 | CFT5W | Compact Fluorescent, twin, (1) 5W lamp | Mag-STD | 1 | 5 | 9
CFT5/2 | CFT5W | Compact Fluorescent, twin, (2) 5W lamp | Mag-STD | 2 | 5 | 18
CFT50/12-BX | CFT50W | Compact Fluorescent, Biax, (12) 50W lamp | Electronic | 12 | 50 | 648
CFT50/1-BX | CFT50W | Compact Fluorescent, Biax, (1) 50W lamp | Electronic | 1 | 50 | 54
CFT50/2-BX | CFT50W | Compact Fluorescent, Biax, (2) 50W lamp | Electronic | 2 | 50 | 108
CFT50/3-BX | CFT50W | Compact Fluorescent, Biax, (3) 50W lamp | Electronic | 3 | 50 | 162
CFT50/4-BX | CFT50W | Compact Fluorescent, Biax, (4) 50W lamp | Electronic | 4 | 50 | 216
CFT50/5-BX | CFT50W | Compact Fluorescent, Biax, (5) 50W lamp | Electronic | 5 | 50 | 270
CFT50/6-BX | CFT50W | Compact Fluorescent, Biax, (6) 50W lamp | Electronic | 6 | 50 | 324
CFT50/8-BX | CFT50W | Compact Fluorescent, Biax, (8) 50W lamp | Electronic | 8 | 50 | 432
CFT50/9-BX | CFT50W | Compact Fluorescent, Biax, (9) 50W lamp | Electronic | 9 | 50 | 486
CFT55/12-BX | CFT55W | Compact Fluorescent, Biax, (12) 55W lamp | Electronic | 12 | 55 | 672
CFT55/1-BX | CFT55W | Compact Fluorescent, Biax, (1) 55W lamp | Electronic | 1 | 55 | 56
CFT55/2-BX | CFT55W | Compact Fluorescent, Biax, (2) 55W lamp | Electronic | 2 | 55 | 112
CFT55/3-BX | CFT55W | Compact Fluorescent, Biax, (3) 55W lamp | Electronic | 3 | 55 | 168
CFT55/4-BX | CFT55W | Compact Fluorescent, Biax, (4) 55W lamp | Electronic | 4 | 55 | 224
CFT55/5-BX | CFT55W | Compact Fluorescent, Biax, (5) 55W lamp | Electronic | 5 | 55 | 280
CFT55/6-BX | CFT55W | Compact Fluorescent, Biax, (6) 55W lamp | Electronic | 6 | 55 | 336
CFT55/6-L | CFT55W | Compact Fluorescent, long Twin, (6) 55W lamp | Electronic | 6 | 55 | 352
CFT55/6-LH | CFT55W | Compact Fluorescent, long Twin, (6) 55W lamp/ High Ballast Factor | Electronic | 6 | 55 | 373 | 2010-10-12 | Changed fixture code from CFT55/6-L to CFT55/6-LH
CFT55/8-BX | CFT55W | Compact Fluorescent, Biax, (8) 55W lamp | Electronic | 8 | 55 | 448
CFT55/8-L | CFT55W | Compact Fluorescent, long Twin, (8) 55W lamp | Electronic | 8 | 55 | 468
CFT55/8-LH | CFT55W | Compact Fluorescent, long Twin, (8) 55W lamp/ High Ballast Factor | Electronic | 8 | 55 | 496 | 2010-10-12 | Changed fixture code from CFT55/8-L to CFT55/8-LH
CFT55/9-BX | CFT55W | Compact Fluorescent, Biax, (9) 55W lamp | Electronic | 9 | 55 | 504
CFT7/1 | CFT7W | Compact Fluorescent, twin, (1) 7W lamp | Mag-STD | 1 | 7 | 10
CFT7/2 | CFT7W | Compact Fluorescent, twin, (2) 7W lamp | Mag-STD | 2 | 7 | 21
CFT9/1 | CFT9W | Compact Fluorescent, twin, (1) 9W lamp | Mag-STD | 1 | 9 | 11
CFT9/2 | CFT9W | Compact Fluorescent, twin, (2) 9W lamp | Mag-STD | 2 | 9 | 23
CFT9/3 | CFT9W | Compact Fluorescent, twin, (3) 9W lamp | Mag-STD | 3 | 9 | 34
Compact Fluorescent Lights (Screw-in)
CFC7/1 | CFC7 | Compact Fluorescent, Screw-in, (1) 7W lamp |  | 1 | 7 | 7 | 2010-03-18 | New Code - From Energy Star
CFC9/1 | CFC9 | Compact Fluorescent, Screw-in, (1) 9W lamp |  | 1 | 9 | 9 | 2010-03-18 | New Code - From Energy Star
CFC11/1 | CFC11 | Compact Fluorescent, Screw-in, (1) 11W lamp |  | 1 | 11 | 11 | 2010-03-18 | New Code - From Energy Star
CFC13/1 | CFC13 | Compact Fluorescent, Screw-in, (1) 13W lamp |  | 1 | 13 | 13 | 2010-03-18 | New Code - From Energy Star
CFC15/1 | CFC15 | Compact Fluorescent, Screw-in, (1) 15W lamp |  | 1 | 15 | 15 | 2010-03-18 | New Code - From Energy Star
CFC18/1 | CFC18 | Compact Fluorescent, Screw-in, (1) 18W lamp |  | 1 | 18 | 18 | 2010-03-18 | New Code - From Energy Star
CFC20/1 | CFC20 | Compact Fluorescent, Screw-in, (1) 20W lamp |  | 1 | 20 | 20 | 2010-03-18 | New Code - From Energy Star
CFC23/1 | CFC23 | Compact Fluorescent, Screw-in, (1) 23W lamp |  | 1 | 23 | 23 | 2010-03-18 | New Code - From Energy Star
CFC26/1 | CFC26 | Compact Fluorescent, Screw-in, (1) 26W lamp |  | 1 | 26 | 26 | 2010-03-18 | New Code - From Energy Star
CFC30/1 | CFC30 | Compact Fluorescent, Screw-in, (1) 30W lamp |  | 1 | 30 | 30 | 2010-03-18 | New Code - From Energy Star
EXIT Sign Fixtures
ECF5/1 | CFT5W | EXIT Compact Fluorescent, (1) 5W lamp | Mag-STD | 1 | 5 | 9
ECF5/2 | CFT5W | EXIT Compact Fluorescent, (2) 5W lamp | Mag-STD | 2 | 5 | 20
ECF7/1 | CFT7W | EXIT Compact Fluorescent, (1) 7W lamp | Mag-STD | 1 | 7 | 10
ECF7/2 | CFT7W | EXIT Compact Fluorescent, (2) 7W lamp | Mag-STD | 2 | 7 | 21
ECF8/1 | F8T5 | EXIT T5 Fluorescent, (1) 8W lamp | Mag-STD | 1 | 8 | 12
ECF8/2 | F8T5 | EXIT T5 Fluorescent, (2) 8W lamp | Mag-STD | 2 | 8 | 24
ECF9/1 | CFT9W | EXIT Compact Fluorescent, (1) 9W lamp | Mag-STD | 1 | 9 | 12
ECF9/2 | CFT9W | EXIT Compact Fluorescent, (2) 9W lamp | Mag-STD | 2 | 9 | 20
EI10/2 | I10 | EXIT Incandescent, (2) 10W lamp |  | 2 | 10 | 20
EI15/1 | I15 | EXIT Incandescent, (1) 15W lamp |  | 1 | 15 | 15
EI15/2 | I15 | EXIT Incandescent, (2) 15W lamp |  | 2 | 15 | 30
EI20/1 | I20 | EXIT Incandescent, (1) 20W lamp |  | 1 | 20 | 20
EI20/2 | I20 | EXIT Incandescent, (2) 20W lamp |  | 2 | 20 | 40
EI25/1 | I25 | EXIT Incandescent, (1) 25W lamp |  | 1 | 25 | 25
EI25/2 | I25 | EXIT Incandescent, (2) 25W lamp |  | 2 | 25 | 50
EI34/1 | I34 | EXIT Incandescent, (1) 34W lamp |  | 1 | 34 | 34
EI34/2 | I34 | EXIT Incandescent, (2) 34W lamp |  | 2 | 34 | 68
EI40/1 | I40 | EXIT Incandescent, (1) 40W lamp |  | 1 | 40 | 40
EI40/2 | I40 | EXIT Incandescent, (2) 40W lamp |  | 2 | 40 | 80
EI5/1 | I5 | EXIT Incandescent, (1) 5W lamp |  | 1 | 5 | 5
EI5/2 | I5 | EXIT Incandescent, (2) 5W lamp |  | 2 | 5 | 10
EI50/2 | I50 | EXIT Incandescent, (2) 50W lamp |  | 2 | 50 | 100
EI7.5/1 | I7.5 | EXIT Tungsten, (1) 7.5 W lamp |  | 1 | 7.5 | 8
EI7.5/2 | I7.5 | EXIT Tungsten, (2) 7.5 W lamp |  | 2 | 7.5 | 15
ELED0.5/1 | LED0.5W | EXIT Light Emitting Diode, (1) 0.5W lamp, Single Sided |  | 1 | 0.5 | 0.5
ELED0.5/2 | LED0.5W | EXIT Light Emitting Diode, (2) 0.5W lamp, Dual Sided |  | 2 | 0.5 | 1
ELED1.5/1 | LED1.5W | EXIT Light Emitting Diode, (1) 1.5W lamp, Single Sided |  | 1 | 1.5 | 1.5
ELED1.5/2 | LED1.5W | EXIT Light Emitting Diode, (2) 1.5W lamp, Dual Sided |  | 2 | 1.5 | 3
ELED10.5/1 | LED10.5W | EXIT Light Emitting Diode, (1) 10.5W lamp, Single Sided |  | 1 | 10.5 | 10.5
ELED10.5/2 | LED10.5W | EXIT Light Emitting Diode, (2) 10.5W lamp, Dual Sided |  | 2 | 10.5 | 21
ELED2/1 | LED2W | EXIT Light Emitting Diode, (1) 2W lamp, Single Sided |  | 1 | 2 | 2
ELED2/2 | LED2W | EXIT Light Emitting Diode, (2) 2W lamp, Dual Sided |  | 2 | 2 | 4
ELED3/1 | LED3W | EXIT Light Emitting Diode, (1) 3W lamp, Single Sided |  | 1 | 3 | 3
ELED3/2 | LED3W | EXIT Light Emitting Diode, (2) 3W lamp, Dual Sided |  | 2 | 3 | 6
ELED5/1 | LED5W | EXIT Light Emitting Diode, (1) 5W lamp, Single Sided |  | 1 | 5 | 5
ELED5/2 | LED5W | EXIT Light Emitting Diode, (2) 5W lamp, Dual Sided |  | 2 | 5 | 10
ELED8/1 | LED8W | EXIT Light Emitting Diode, (1) 8W lamp, Single Sided |  | 1 | 8 | 8
ELED8/2 | LED8W | EXIT Light Emitting Diode, (2) 8W lamp, Dual Sided |  | 2 | 8 | 16
Linear Fluorescent Fixtures
F1.51LS | F15T8 | Fluorescent, (1) 18" T8 lamp | Mag-STD | 1 | 15 | 19
F1.51SS | F15T12 | Fluorescent, (1) 18" T12 lamp | Mag-STD | 1 | 15 | 19
F1.52LS | F15T8 | Fluorescent, (2) 18" T8 lamp | Mag-STD | 2 | 15 | 36
F1.52SS | F15T12 | Fluorescent, (2) 18", T12 lamp | Mag-STD | 2 | 15 | 36
F21HS | F24T12/HO | Fluorescent, (1) 24", HO lamp | Mag-STD | 1 | 35 | 62
F21ILL | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 17 | 20
F21ILL/T2 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 17 | 17
F21ILL/T2-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 2 Lamp Ballast | Electronic | 1 | 17 | 15
F21ILL/T3 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 17 | 16
F21ILL/T3-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 3 Lamp Ballast | Electronic | 1 | 17 | 14
F21ILL/T4 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 17 | 15
F21ILL/T4-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 1 | 17 | 14
F21LL | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 17 | 16
F21LL/T2 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 17 | 16
F21LL/T3 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 17 | 17
F21LL/T4 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 17 | 17
F21LL-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 17 | 15
F21LS | F17T8 | Fluorescent, (1) 24", T8 lamp, Standard Ballast | Mag-STD | 1 | 17 | 24
F21GL | F24T5 | Fluorescent, (1) 24", STD T5 lamp | Electronic | 1 | 14 | 18
F21SE | F20T12 | Fluorescent, (1) 24", STD lamp | Mag-ES | 1 | 20 | 26
F21SS | F20T12 | Fluorescent, (1) 24", STD lamp | Mag-STD | 1 | 20 | 28
F21GHL | F24T5/HO | Fluorescent, (1) 24", STD HO T5 lamp | Electronic | 1 | 24 | 29
F22SHS | F24T12/HO | Fluorescent, (2) 24", HO lamp | Mag-STD | 2 | 35 | 90
F22GHL | F24T5/HO | Fluorescent, (2) 24", STD HO T5 lamp | Electronic | 2 | 24 | 55
F22ILE | F17T8 | Fluorescent, (2) 24", T-8 Instant Start lamp, Energy Saving Magnetic Ballast | Mag-ES | 2 | 17 | 45
F22ILL | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 17 | 33
F22ILL/T4 | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 17 | 31
F22ILL/T4-R | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 2 | 17 | 28
F22ILL-R | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 17 | 29
F22LL | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 17 | 31
F22LL/T4 | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 17 | 34
F22LL-R | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 2 | 17 | 28
F22GL | F24T5 | Fluorescent, (2) 24", STD T5 lamp | Electronic | 2 | 14 | 35
F22SE | F20T12 | Fluorescent, (2) 24", STD lamp | Mag-ES | 2 | 20 | 51
F22SS | F20T12 | Fluorescent, (2) 24", STD lamp | Mag-STD | 2 | 20 | 56
F23ILL | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 17 | 47
F23ILL-H | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 3 | 17 | 49
F23ILL-R | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 17 | 43
F23LL | F17T8 | Fluorescent, (3) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 17 | 52
F23LL-R | F17T8 | Fluorescent, (3) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 3 | 17 | 41
F23SE | F20T12 | Fluorescent, (3) 24", STD lamp | Mag-ES | 3 | 20 | 77
F23SS | F20T12 | Fluorescent, (3) 24", STD lamp | Mag-STD | 3 | 20 | 84
F24ILL | F17T8 | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 17 | 61
F24ILL-R | F17T8 | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 17 | 55
F24LL | F17T8 | Fluorescent, (4) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 17 | 68
F24LL-R | F17T8 | Fluorescent, (4) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 4 | 17 | 57
F24SE | F20T12 | Fluorescent, (4) 24", STD lamp | Mag-ES | 4 | 20 | 102
F24SS | F20T12 | Fluorescent, (4) 24", STD lamp | Mag-STD | 4 | 20 | 112
F26SE | F20T12 | Fluorescent, (6) 24", STD lamp | Mag-ES | 6 | 20 | 153
F26SS | F20T12 | Fluorescent, (6) 24", STD lamp | Mag-STD | 6 | 20 | 168
F31EE | F30T12/ES | Fluorescent, (1) 36", ES lamp | Mag-ES | 1 | 25 | 38
F31EE/T2 | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem wired | Mag-ES | 1 | 25 | 33
F31EL | F30T12/ES | Fluorescent, (1) 36", ES lamp | Electronic | 1 | 25 | 26
F31ES | F30T12/ES | Fluorescent, (1) 36", ES lamp | Mag-STD | 1 | 25 | 42
F31ES/T2 | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem wired | Mag-STD | 1 | 25 | 37
F31ILL | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 25 | 26
F31ILL/T2 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 25 | 23
F31ILL/T2-H | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (BF: .96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 25 | 24
F31ILL/T2-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 25 | 23
F31ILL/T3 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 25 | 22
F31ILL/T3-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 3 Lamp Ballast | Electronic | 1 | 25 | 22
F31ILL/T4 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 25 | 22
F31ILL/T4-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 1 | 25 | 22
F31ILL-H | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 25 | 28
F31ILL-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 25 | 27
F31LL | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 25 | 24
F31LL/T2 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 25 | 23
F31LL/T3 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 25 | 24
F31LL/T4 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 25 | 22
F31LL-H | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 25 | 26
F31LL-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 25 | 23
F31SE/T2 | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem wired | Mag-ES | 1 | 30 | 37
F31GHL | F36T5/HO | Fluorescent, (1) 36", STD HO T5 lamp | Electronic | 1 | 39 | 43
F31SHS | F36T12/HO | Fluorescent, (1) 36", HO lamp | Mag-STD | 1 | 50 | 70
F31SL | F30T12 | Fluorescent, (1) 36", STD lamp | Electronic | 1 | 30 | 31
F31GL | F36T5 | Fluorescent, (1) 36", STD T5 lamp | Electronic | 1 | 21 | 27
F31SS | F30T12 | Fluorescent, (1) 36", STD lamp | Mag-STD | 1 | 30 | 46
F31SS/T2 | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem wired | Mag-STD | 1 | 30 | 41
F32EE | F30T12/ES | Fluorescent, (2) 36", ES lamp | Mag-ES | 2 | 25 | 66
F32EL | F30T12/ES | Fluorescent, (2) 36", ES lamp | Electronic | 2 | 25 | 50
F32ES | F30T12/ES | Fluorescent, (2) 36", ES lamp | Mag-STD | 2 | 25 | 73
F32ILL | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 25 | 46
F32ILL/T4 | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 25 | 44
F32ILL/T4-R | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 2 | 25 | 43
F32ILL-H | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 2 | 25 | 48
F32ILL-R | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 25 | 46
F32LE | F25T8 | Fluorescent, (2) 36", T-8 lamp | Mag-ES | 2 | 25 | 65
F32LL | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 25 | 46
F32LL/T4 | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 25 | 45
F32LL-H | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 2 | 25 | 50
F32LL-R | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 2 | 25 | 42
F32LL-V | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, VHLO (BF>1.1) | Electronic | 2 | 25 | 70
F32SE | F30T12 | Fluorescent, (2) 36", STD lamp | Mag-ES | 2 | 30 | 74
F32GHL | F36T5/HO | Fluorescent, (2) 36", STD HO T5 lamp | Electronic | 2 | 39 | 85 | 2010-10-12 | Changed description from 1 lamp to 2 lamps
F32SHS | F36T12/HO | Fluorescent, (2) 36", HO, lamp | Mag-STD | 2 | 50 | 114
F32SL | F30T12 | Fluorescent, (2) 36", STD lamp | Electronic | 2 | 30 | 58
F32GL | F36T5 | Fluorescent, (1) 36", STD T5 lamp | Electronic | 2 | 21 | 52
F32SS | F30T12 | Fluorescent, (2) 36", STD lamp | Mag-STD | 2 | 30 | 81
F33EE | F30T12/ES | Fluorescent, (3) 36", ES lamp | Mag-ES | 3 | 25 | 104 | 2010-03-18 | New Code - F31EE + F32EE
F33EL | F30T12/ES | Fluorescent, (3) 36", ES lamp | Electronic | 3 | 25 | 76 | 2010-03-18 | New Code - F31EL + F32EL
F33ES | F30T12/ES | Fluorescent, (3) 36", ES lamp | Mag-STD | 3 | 25 | 115
F33ILL | F25T8 | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 25 | 67
F33ILL-R | F25T8 | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 25 | 66
F33LL | F25T8 | Fluorescent, (3) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 25 | 72
F33LL-R | F25T8 | Fluorescent, (3) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 3 | 25 | 62
F33SE | F30T12 | Fluorescent, (3) 36", STD lamp, (1) STD ballast and (1) ES ballast | Mag-ES | 3 | 30 | 120
F33SS | F30T12 | Fluorescent, (3) 36", STD lamp | Mag-STD | 3 | 30 | 127
F34EE | F30T12/ES | Fluorescent, (4) 36", ES lamp | Mag-ES | 4 | 25 | 132 | 2010-03-18 | New Code - F32EE x 2
F34EL | F30T12/ES | Fluorescent, (4) 36", ES lamp | Electronic | 4 | 25 | 100 | 2010-03-18 | New Code - F32EL x 2
F34ILL | F25T8 | Fluorescent, (4) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 25 | 87
F34ILL-R | F25T8 | Fluorescent, (4) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 25 | 86
F34LL | F25T8 | Fluorescent, (4) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 25 | 89
F34LL-R | F25T8 | Fluorescent, (4) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 4 | 25 | 84
F34SE | F30T12 | Fluorescent, (4) 36", STD lamp | Mag-ES | 4 | 30 | 148
F34SL | F30T12 | Fluorescent, (4) 36", STD lamp | Electronic | 4 | 30 | 116
F34SS | F30T12 | Fluorescent, (4) 36", STD lamp | Mag-STD | 4 | 30 | 162
F36EE | F30T12/ES | Fluorescent, (6) 36", ES lamp | Mag-ES | 6 | 25 | 198
F36ILL-R | F25T8 | Fluorescent, (6) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85) | Electronic | 6 | 25 | 134
F36SE | F30T12 | Fluorescent, (6) 36", STD lamp | Mag-ES | 6 | 30 | 238
F40EE/D1 | None | Fluorescent, (0) 48" lamp, Completely delamped fixture with (1) hot ballast | Mag-ES | 0 | 0 | 4
F40EE/D2 | None | Fluorescent, (0) 48" lamp, Completely delamped fixture with (2) hot ballast | Mag-ES | 0 | 0 | 8
F41EE | F40T12/ES | Fluorescent, (1) 48", ES lamp | Mag-ES | 1 | 34 | 43
F41EE/D2 | F40T12/ES | Fluorescent, (1) 48", ES lamp, 2 ballast | Mag-ES | 1 | 34 | 43
F41EE/T2 | F40T12/ES | Fluorescent, (1) 48", ES lamp, tandem wired, 2-lamp ballast | Mag-ES | 1 | 34 | 36
F41EHS | F48T12/HO/ES | Fluorescent, (1) 48", ES HO lamp | Mag-STD | 1 | 55 | 80
F41EIS | F48T12/ES | Fluorescent, (1) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 1 | 30 | 51
F41EL | F40T12/ES | Fluorescent, (1) 48", T12 ES lamp, Electronic Ballast | Electronic | 1 | 34 | 32
F41EL/T2 | F40T12/ES | Fluorescent, (1) 48", T-12 ES lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 34 | 32
F41ES | F40T12/ES | Fluorescent, (1) 48", ES lamp | Mag-STD | 1 | 34 | 50
F41EVS | F48T12/VHO/ES | Fluorescent, (1) 48", VHO ES lamp | Mag-STD | 1 |  | 123
F41IAL | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start Ballast | Electronic | 1 | 25 | 25
F41IAL/T2-R | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start, Tandem 2-Lamp Ballast, RLO (BF<0.85) | Electronic | 1 | 25 | 19
F41IAL/T3-R | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start, Tandem 3-Lamp Ballast, RLO (BF<0.85) | Electronic | 1 | 25 | 20
F41ILL | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 32 | 31
F41SILL | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 30 | 28
F41SILL/T2 | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 30 | 27
F41SILL/T3 | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 30 | 27
F41SILL/T4 | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 30 | 26
F41SILL-R | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 30 | 25
F41SILL/T2-R | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 30 | 24
F41SILL/T3-R | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 30 | 24
F41SILL/T4-R | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 30 | 23
F41SILL-H | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 30 | 37
F41SILL/T2-H | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 30 | 36
F41SILL/T3-H | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 30 | 36
F41SSILL | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 28 | 26
F41SSILL/T2 | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 28 | 25
F41SSILL/T3 | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 28 | 25
F41SSILL/T4 | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 28 | 24
F41SSILL-R | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 28 | 23
F41SSILL/T2-R | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 28 | 22
F41SSILL/T3-R | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 28 | 22
F41SSILL/T4-R | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 28 | 21
F41SSILL-H | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 28 | 33
F41SSILL/T2-H | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 28 | 32
F41SSILL/T3-H | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 28 | 32
F41ILL/T2 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 30
F41ILL/T2-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 33
F41ILL/T2-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 26
F41ILL/T3 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 30
F41ILL/T3-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 31
F41ILL/T3-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 26
F41ILL/T4 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 32 | 28
F41ILL/T4-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 32 | 26
F41ILL-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 32 | 36
F41LE | F32T8 | Fluorescent, (1) 48", T-8 lamp | Mag-ES | 1 | 32 | 35
F41LL | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 32 | 32
F41LL/T2 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 30
F41LL/T2-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 39
F41LL/T2-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 32 | 27
F41LL/T3 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 31
F41LL/T3-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 33
F41LL/T3-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 32 | 25
F41LL/T4 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 32 | 30
F41LL/T4-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 32 | 26
F41LL-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 32 | 39
F41LL-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 32 | 27
F41SE | F40T12 | Fluorescent, (1) 48", STD lamp | Mag-ES | 1 | 40 | 50
F41GHL | F48T5/HO | Fluorescent, (1) 48", STD HO T5 lamp | Electronic | 1 | 54 | 59
F41SHS | F48T12/HO | Fluorescent, (1) 48", STD HO lamp | Mag-STD | 1 | 60 | 85
F41SIL | F48T12 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast | Electronic | 1 | 39 | 46
F41SIL/T2 | F48T12 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast, tandem wired | Electronic | 1 | 39 | 37
F41SIS | F48T12 | Fluorescent, (1) 48", STD IS lamp | Mag-STD | 1 | 39 | 60
F41SIS/T2 | F48T12 | Fluorescent, (1) 48", STD IS lamp, tandem to 2-lamp ballast | Mag-STD | 1 | 39 | 52
F41GL | F48T5 | Fluorescent, (1) 48", STD T5 lamp | Electronic | 1 | 28 | 32
F41SL/T2 | F40T12 | Fluorescent, (1) 48", T-12 STD lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 40 | 36
F41SS | F40T12 | Fluorescent, (1) 48", STD lamp | Mag-STD | 1 | 40 | 57
F41SVS | F48T12/VHO | Fluorescent, (1) 48", STD VHO lamp | Mag-STD | 1 | 110 | 135
F41TS | F40T10 | Fluorescent, (1) 48", T-10 lamp | Mag-STD | 1 | 40 | 51
F42EE | F40T12/ES | Fluorescent, (2) 48", ES lamp | Mag-ES | 2 | 34 | 72
F42EE/D2 | F40T12/ES | Fluorescent, (2) 48", ES lamp, 2 Ballasts (delamped) | Mag-ES | 2 | 34 | 76
F42EHS | F48T12/HO/ES | Fluorescent, (2) 42", HO lamp (3.5' lamp) | Mag-STD | 2 | 55 | 135
F42EIS | F48T12/ES | Fluorescent, (2) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 2 | 30 | 82
F42EL | F40T12/ES | Fluorescent, (2) 48", T12 ES lamps, Electronic Ballast | Electronic | 2 | 34 | 60
F42ES | F40T12/ES | Fluorescent, (2) 48", ES lamp | Mag-STD | 2 | 34 | 80
F42EVS | F48T12/VHO/ES | Fluorescent, (2) 48", VHO ES lamp | Mag-STD | 2 |  | 210
F42IAL/T4-R | F25T12 | Fluorescent, (2) 48", F25T12 lamp, Instant Start, Tandem 4-Lamp Ballast, RLO (BF<0.85) | Electronic | 2 | 25 | 40
F42IAL-R | F25T12 | Fluorescent, (2) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 25 | 39
F42ILL | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 32 | 59
F42SILL | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 30 | 53
F42SILL/T4 | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 30 | 52 | 2010-10-12 | Changed fixture code from F41SILL/T4 to F42SILL/T4
F42SILL-R | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 30 | 47
F42SILL/T4-R | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 2 | 30 | 46 | 2010-10-12 | Changed fixture code from F41SILL/T4-R to F42SILL/T4-R
F42SILL-H | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-2.2) | Electronic | 2 | 30 | 72
F42SSILL | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 28 | 48
F42SSILL/T4 | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 28 | 47 | 2010-10-12 | Changed fixture code from F41SSILL/T4 to F42SSILL/T4
F42SSILL-R | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 28 | 45
F42SSILL/T4-R | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 2 | 28 | 44 | 2010-10-12 | Changed fixture code from F41SSILL/T4-R to F42SSILL/T4-R
F42SSILL-H | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-2.2) | Electronic | 2 | 28 | 67
F42ILL/T4 | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 32 | 56
F42ILL/T4-R | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 2 | 32 | 51
F42ILL-H | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 2 | 32 | 65
F42ILL-R | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 32 | 52
F42ILL-V | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 2 | 32 | 79
F42LE | F32T8 | Fluorescent, (2) 48", T-8 lamp | Mag-ES | 2 | 32 | 71
F42LL | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 32 | 60
F42LL/T4 | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 2 | 32 | 59
F42LL/T4-R | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 2 | 32 | 53
F42LL-H | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 2 | 32 | 70
F42LL-R | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 2 | 32 | 54
F42LL-V | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, VHLO (BF>1.1) | Electronic | 2 | 32 | 85
F42SE | F40T12 | Fluorescent, (2) 48", STD lamp | Mag-ES | 2 | 40 | 86
F42GHL | F48T5/HO | Fluorescent, (2) 48", STD HO T5 lamp | Electronic | 2 | 54 | 117
F42SHS | F48T12/HO | Fluorescent, (2) 48", STD HO lamp | Mag-STD | 2 | 60 | 145
F42SIL | F48T12 | Fluorescent, (2) 48", STD IS lamp, Electronic ballast | Electronic | 2 | 39 | 74
F42SIS | F48T12 | Fluorescent, (2) 48", STD IS lamp | Mag-STD | 2 | 39 | 103
F42GL | F48T5 | Fluorescent, (2) 48", STD T5 lamp | Electronic | 2 | 28 | 63
F42SS | F40T12 | Fluorescent, (2) 48", STD lamp | Mag-STD | 2 | 40 | 94
F42SVS | F48T12/VHO | Fluorescent, (2) 48", STD VHO lamp | Mag-STD | 2 | 110 | 242
F43EE | F40T12/ES | Fluorescent, (3) 48", ES lamp | Mag-ES | 3 | 34 | 115
F43EHS | F48T12/HO/ES | Fluorescent, (3) 48", ES HO lamp (3.5' lamp) | Mag-STD | 3 | 55 | 215
F43EIS | F48T12/ES | Fluorescent, (3) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 3 | 30 | 133
F43EL | F40T12/ES | Fluorescent, (3) 48", T12 ES lamps, Electronic Ballast | Electronic | 3 | 34 | 92
F43ES | F40T12/ES | Fluorescent, (3) 48", ES lamp | Mag-STD | 3 | 34 | 130
F43EVS | F48T12/VHO/ES | Fluorescent, (3) 48", VHO ES lamp | Mag-STD | 3 |  | 333
F43IAL-R | F25T12 | Fluorescent, (3) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 25 | 60
F43ILL | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 32 | 89
F43SILL | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 30 | 78
F43SILL-R | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 30 | 70
F43SILL-H | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-3.3) | Electronic | 3 | 30 | 105
F43SSILL | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 28 | 72
F43SSILL-R | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 28 | 66
F43SSILL-H | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-3.3) | Electronic | 3 | 28 | 98
F43ILL/2 | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 3 | 32 | 90
F43ILL-H | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 3 | 32 | 93
F43ILL-R | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 3 | 32 | 78
F43ILL-V | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 3 | 32 | 112
F43LE | F32T8 | Fluorescent, (3) 48", T-8 lamp | Mag-ES | 3 | 32 | 110
F43LL | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 32 | 93
F43LL/2 | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 3 | 32 | 92
F43LL-H | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 3 | 32 | 98
F43LL-R | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 3 | 32 | 76
F43SE | F40T12 | Fluorescent, (3) 48", STD lamp | Mag-ES | 3 | 40 | 136
F43GHL | F48T5/HO | Fluorescent, (3) 48", STD HO T5 lamp | Electronic | 3 | 54 | 177
F43SHS | F48T12/HO | Fluorescent, (3) 48", STD HO lamp | Mag-STD | 3 | 60 | 230
F43SIL | F40T12 | Fluorescent, (3) 48", STD IS lamp, Electronic ballast | Electronic | 3 | 39 | 120
F43SIS | F48T12 | Fluorescent, (3) 48", STD IS lamp | Mag-STD | 3 | 39 | 162
F43SS | F40T12 | Fluorescent, (3) 48", STD lamp | Mag-STD | 3 | 40 | 151
F43SVS | F48T12/VHO | Fluorescent, (3) 48", STD VHO lamp | Mag-STD | 3 | 110 | 377
F44EE | F40T12/ES | Fluorescent, (4) 48", ES lamp | Mag-ES | 4 | 34 | 144
F44EE/D4 | F40T12/ES | Fluorescent, (4) 48", ES lamp, 4 Ballasts (delamped) | Mag-ES | 4 | 34 | 152
F44EHS | F48T12/HO/ES | Fluorescent, (4) 48", ES HO lamp | Mag-STD | 4 | 55 | 270
F44EIS | F48T12/ES | Fluorescent, (4) 48" ES Instant Start lamp, Magnetic ballast | Mag-STD | 4 | 30 | 164
F44EL | F40T12/ES | Fluorescent, (4) 48", T12 ES lamp, Electronic Ballast | Electronic | 4 | 34 | 120
F44ES | F40T12/ES | Fluorescent, (4) 48", ES lamp | Mag-STD | 4 | 34 | 160
F44EVS | F48T12/VHO/ES | Fluorescent, (4) 48", VHO ES lamp | Mag-STD | 4 |  | 420
F44IAL-R | F25T12 | Fluorescent, (4) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 25 | 80
F44ILL | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 32 | 112
F44SILL | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 30 | 105
F44SILL-R | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 30 | 91
F44SILL-H | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-4.4) | Electronic | 4 | 30 | 140
F44SSILL | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 28 | 96
F44SSILL-R | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 28 | 86
F44SSILL-H | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-4.4) | Electronic | 4 | 28 | 131
F44ILL/2 | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 4 | 32 | 118
F44ILL-R | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 4 | 32 | 102
F44LE | F32T8 | Fluorescent, (4) 48", T-8 lamp | Mag-ES | 4 | 32 | 142
F44LL | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 32 | 118
F44LL/2 | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 4 | 32 | 120
F44LL-R | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 4 | 32 | 105
F44SE | F40T12 | Fluorescent, (4) 48", STD lamp | Mag-ES | 4 | 40 | 172
F44GHL | F48T5/HO | Fluorescent, (4) 48", STD HO T5 lamp | Electronic | 4 | 54 | 234
F44SHS | F48T12/HO | Fluorescent, (4) 48", STD HO lamp | Mag-STD | 4 | 60 | 290
F44SIL | F48T12 | Fluorescent, (4) 48", STD IS lamp, Electronic ballast | Electronic | 4 | 39 | 148
F44SIS | F48T12 | Fluorescent, (4) 48", STD IS lamp | Mag-STD | 4 | 39 | 204
F44SS | F40T12 | Fluorescent, (4) 48", STD lamp | Mag-STD | 4 | 40 | 188
F44SVS | F48T12/VHO | Fluorescent, (4) 48", STD VHO lamp | Mag-STD | 4 | 110 | 484
F45ILL | F32T8 | Fluorescent, (5) 48", T-8 lamp, (1) 3-lamp IS ballast and (1) 2-lamp IS ballast, NLO (BF: .85-.95) | Electronic | 5 | 32 | 148
F45GHL | F48T5/HO | Fluorescent, (5) 48", STD HO T5 lamp | Electronic | 5 | 54 | 294
F46EE | F40T12/ES | Fluorescent, (6) 48", ES lamp | Mag-ES | 6 | 34 | 216
F46EL | F40T12/ES | Fluorescent, (6) 48", ES lamp | Electronic | 6 | 34 | 186
F46ES | F40T12/ES | Fluorescent, (6) 48", ES lamp | Mag-STD | 6 | 34 | 236
F46EHS | F48T12/HO/ES | Fluorescent, (6) 48", ES HO lamp (3.5' lamp) | Mag-STD | 6 | 55 | 405 | 2010-03-18 | New Code - F42EHS + F44EHS
F46ILL | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 6 | 32 | 175
F46ILL-R | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, RLO (BF< .85) | Electronic | 6 | 32 | 156
F46LL | F32T8 | Fluorescent, (6) 48", T-8 lamp, NLO (BF: .85-.95) | Electronic | 6 | 32 | 182
F46GHL | F48T5/HO | Fluorescent, (6) 48", STD HO T5 lamp | Electronic | 6 | 54 | 351
F46SE | F40T12 | Fluorescent, (6) 48", STD lamp | Mag-ES | 6 | 40 | 258
F46SS | F40T12 | Fluorescent, (6) 48", STD lamp | Mag-STD | 6 | 40 | 282
F48EE | F40T12/ES | Fluorescent, (8) 48", ES lamp | Mag-ES | 8 | 34 | 288
F48EHS | F48T12/HO/ES | Fluorescent, (8) 48", ES HO lamp (3.5' lamp) | Mag-STD | 8 | 55 | 540 | 2010-03-18 | New Code - F44EHS x 2
F48ILL | F32T8 | Fluorescent, (8) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 8 | 32 | 224
F48ILL-R | F32T8 | Fluorescent, (8) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 8 | 32 | 204
F48GHL | F48T5/HO | Fluorescent, (8) 48", STD HO T5 lamp | Electronic | 8 | 54 | 468
F51ILHL | F60T12/HO | Fluorescent, (1) 60", T-8 HO lamp, Instant Start Ballast | Electronic | 1 | 55 | 59
F51ILL | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 40 | 36
F51ILL/T2 | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 40 | 36
F51ILL/T3 | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 40 | 35
F51ILL/T4 | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 40 | 34
F51ILL-R | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 40 | 43
F51SHE | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-ES | 1 | 75 | 88
F51SHL | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Electronic | 1 | 75 | 69
| F60T5/HO | Fluorescent, (1) 60", STD HO T5 lamp | Electronic | 1 | 49 | 54 | 2010-10-12 | Deleted F51GHL - 5-foot HO T-5s are typically 80 watts
F51GHL | F60T5/HO | Fluorescent, (1) 60", STD HO T5 lamp | Electronic | 1 | 80 | 89
F51SHS | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-STD | 1 | 75 | 92
F51SL | F60T12 | Fluorescent, (1) 60", STD lamp | Electronic | 1 | 50 | 44
F51GL | F60T5 | Fluorescent, (1) 60", STD T5 lamp | Electronic | 1 | 35 | 39
F51SS | F60T12 | Fluorescent, (1) 60", STD lamp | Mag-STD | 1 | 50 | 63
F51SVS | F60T12/VHO | Fluorescent, (1) 60", VHO ES lamp | Mag-STD | 1 | 135 | 165
F52ILHL | F60T12/HO | Fluorescent, (2) 60", T-8 HO lamp, Instant Start Ballast | Electronic | 2 | 55 | 123
F52ILL | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 40 | 72
F52ILL/T4 | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 2 | 40 | 67
F52ILL-H | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 2 | 40 | 80
F52ILL-R | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 40 | 73
F52SHE | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Mag-ES | 2 | 75 | 176
F52SHL | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Electronic | 2 | 75 | 138
| F60T5/HO | Fluorescent, (2) 60", STD HO T5 lamp | Electronic | 2 | 49 | 106 | 2010-10-12 | Deleted F52GHL - 5-foot HO T-5s are typically 80 watts
F52SHS | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Mag-STD | 2 | 75 | 168
F52SL | F60T12 | Fluorescent, (2) 60", STD lamp | Electronic | 2 | 50 | 88
F52GL | F60T5 | Fluorescent, (2) 60", STD T5 lamp | Electronic | 2 | 35 | 76
F52SS | F60T12 | Fluorescent, (2) 60", STD lamp | Mag-STD | 2 | 50 | 128
F52SVS | F60T12/VHO | Fluorescent, (2) 60", VHO ES lamp | Mag-STD | 2 | 135 | 310
F53ILL | F40T8 | Fluorescent, (3) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 40 | 106
F53ILL-H | F40T8 | Fluorescent, (3) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 3 | 40 | 108
F54ILL | F40T8 | Fluorescent, (4) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 40 | 134
F54ILL-H | F40T8 | Fluorescent, (4) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 4 | 40 | 126
F61ISL | F72T12 | Fluorescent, (1) 72", STD lamp, IS electronic ballast | Electronic | 1 | 55 | 68
F61SE | F72T12 | Fluorescent, (1) 72", STD lamp | Mag-ES | 1 | 55 | 76
F61SHS | F72T12/HO | Fluorescent, (1) 72", STD HO lamp | Mag-STD | 1 | 85 | 120
F61SS | F72T12 | Fluorescent, (1) 72", STD lamp | Mag-STD | 1 | 55 | 90
F61SVS | F72T12/VHO | Fluorescent, (1) 72", VHO lamp | Mag-STD | 1 | 160 | 180
F62ILHL | F72T8 | Fluorescent, (2) 72", T-8 HO lamp, Instant Start Ballast | Electronic | 2 | 65 | 147
F62ISL | F72T12 | Fluorescent, (2) 72", STD lamp, IS electronic ballast | Electronic | 2 | 55 | 108
F62SE | F72T12 | Fluorescent, (2) 72", STD lamp | Mag-ES | 2 | 55 | 122
F62SHE | F72T12/HO | Fluorescent, (2) 72", STD HO lamp | Mag-ES | 2 | 85 | 194
F62SHS | F72T12/HO | Fluorescent, (2) 72", STD HO lamp | Mag-STD | 2 | 85 | 220
F62SL | F72T12 | Fluorescent, (2) 72", STD lamp | Electronic | 2 | 55 | 108
F62SS | F72T12 | Fluorescent, (2) 72", STD lamp | Mag-STD | 2 | 55 | 145
F62SVS | F72T12/VHO | Fluorescent, (2) 72", VHO lamp | Mag-STD | 2 | 160 | 330
F63ISL | F72T12 | Fluorescent, (3) 72", STD lamp, IS electronic ballast | Electronic | 3 | 55 | 176
F63SS | F72T12 | Fluorescent, (3) 72", STD lamp | Mag-STD | 3 | 55 | 202
F64ISL | F72T12 | Fluorescent, (4) 72", STD lamp, IS electronic ballast | Electronic | 4 | 55 | 216
F64SE | F72T12 | Fluorescent, (4) 72", STD lamp | Mag-ES | 4 | 55 | 230
F64SHE | F72T12/HO | Fluorescent, (4) 72", STD HO lamp | Mag-ES | 4 | 85 | 388
F64SS | F72T12 | Fluorescent, (4) 72", STD lamp | Mag-STD | 4 | 55 | 244
F81EE | F96T12/ES | Fluorescent, (1) 96", ES lamp | Mag-ES | 1 | 60 | 61 | 2010-03-18 | New Code - F82EE / 2
F81EE/T2 | F96T12/ES | Fluorescent, (1) 96", ES lamp, tandem to 2-lamp ballast | Mag-ES | 1 | 60 | 62
F81EHL | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Electronic | 1 | 95 | 80
F81EHL/T2 | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 95 | 85
F81EHS | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Mag-STD | 1 | 95 | 125
F81EL | F96T12/ES | Fluorescent, (1) 96", ES lamp | Electronic | 1 | 60 | 60
F81EL/T2 | F96T12/ES | Fluorescent, (1) 96", ES lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 60 | 55
F81ES | F96T12/ES | Fluorescent, (1) 96", ES lamp | Mag-STD | 1 | 60 | 83
F81ES/T2 | F96T12/ES | Fluorescent, (1) 96", ES lamp, tandem to 2-lamp ballast | Mag-STD | 1 | 60 | 64
F81EVS | F96T12/VHO/ES | Fluorescent, (1) 96", ES VHO lamp | Mag-STD | 1 | 185 | 200
F81ILL | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 59 | 58
F81ILL/T2 | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 59 | 55
F81ILL/T2-R | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 2 Lamp Ballast | Electronic | 1 | 59 | 49
F81ILL-H | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 59 | 68
F81ILL-R | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 59 | 57
F81ILL-V | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 1 | 59 | 71
F81LHL | F96T8/HO | Fluorescent, (1) 96", T8 HO lamp | Electronic | 1 | 86 | 85
F81LHL/T2 | F96T8/HO | Fluorescent, (1) 96", T8 HO lamp, tandem wired to 2-lamp ballast | Electronic | 1 | 86 | 80
F81SE | F96T12 | Fluorescent, (1) 96", STD lamp | Mag-ES | 1 | 75 | 91
| F96T12/HO | Fluorescent, (1) 96", ES HO lamp | Mag-STD | 1 | 95 | 125 | 2010-10-12 | Deleted F81EHS - repeat fixture, lamp code is incorrect
F81SHE | F96T12/HO | Fluorescent, (1) 96", STD HO lamp | Mag-ES | 1 | 110 | 132
F81SHL/T2 | F96T12/HO | Fluorescent, (1) 96", STD HO lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 110 | 98
F81SHS | F96T12/HO | Fluorescent, (1) 96", STD HO lamp | Mag-STD | 1 | 110 | 145
F81SL | F96T12 | Fluorescent, (1) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 75 | 70
F81SL/T2 | F96T12 | Fluorescent, (1) 96", STD lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 75 | 67
F81SS | F96T12 | Fluorescent, (1) 96", STD lamp | Mag-STD | 1 | 75 | 100
F81SVS | F96T12/VHO | Fluorescent, (1) 96", STD VHO lamp | Mag-STD | 1 | 215 | 230
F82EE | F96T12/ES | Fluorescent, (2) 96", ES lamp | Mag-ES | 2 | 60 | 123
F82EHE | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Mag-ES | 2 | 95 | 207
F82EHL | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Electronic | 2 | 95 | 170
F82EHS | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Mag-STD | 2 | 95 | 227
F82EL | F96T12/ES | Fluorescent, (2) 96", ES lamp | Electronic | 2 | 60 | 110
F82ES | F96T12/ES | Fluorescent, (2) 96", ES lamp | Mag-STD | 2 | 60 | 138
F82EVS | F96T12/VHO/ES | Fluorescent, (2) 96", ES VHO lamp | Mag-STD | 2 | 185 | 390
F82ILL | F96T8 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 59 | 109
F82ILL-R | F96T8 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 2 | 59 | 98
F82LHL | F96T8/HO | Fluorescent, (2) 96", T8 HO lamp | Electronic | 2 | 86 | 160
F82SE | F96T12 | Fluorescent, (2) 96", STD lamp | Mag-ES | 2 | 75 | 158
F82SHE | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Mag-ES | 2 | 110 | 237
F82SHL | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Electronic | 2 | 110 | 195
F82SHS | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Mag-STD | 2 | 110 | 257
F82SL | F96T12 | Fluorescent, (2) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 2 | 75 | 134
F82SS | F96T12 | Fluorescent, (2) 96", STD lamp | Mag-STD | 2 | 75 | 173
F82SVS | F96T12/VHO | Fluorescent, (2) 96", STD VHO lamp | Mag-STD | 2 | 215 | 450
F83EE | F96T12/ES | Fluorescent, (3) 96", ES lamp | Mag-ES | 3 | 60 | 210
F83EHE | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamp, (1) 2-lamp ES Ballast, (1) 1-lamp STD Ballast | Mag-ES/STD | 3 | 95 | 319
F83EHS | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamp | Mag-STD | 3 | 95 | 352
F83EL | F96T12/ES | Fluorescent, (3) 96", ES lamp | Electronic | 3 | 60 | 179
F83ES | F96T12/ES | Fluorescent, (3) 96", ES lamp | Mag-STD | 3 | 60 | 221
F83EVS | F96T12/VHO/ES | Fluorescent, (3) 96", ES VHO lamp | Mag-STD | 3 | 185 | 590
F83ILL | F96T8 | Fluorescent, (3) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 3 | 59 | 167
F83SHS | F96T12/HO | Fluorescent, (3) 96", STD HO lamp | Mag-STD | 3 | 110 | 392
F83SS | F96T12 | Fluorescent, (3) 96", STD lamp | Mag-STD | 3 | 75 | 273
F83SVS | F96T12/VHO | Fluorescent, (3) 96", STD VHO lamp | Mag-STD | 3 | 215 | 680
F84EE | F96T12/ES | Fluorescent, (4) 96", ES lamp | Mag-ES | 4 | 60 | 246
F84EHE | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Mag-ES | 4 | 95 | 414
F84EHL | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Electronic | 4 | 95 | 340
F84EHS | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Mag-STD | 4 | 95 | 454
F84EL | F96T12/ES | Fluorescent, (4) 96", ES lamp | Electronic | 4 | 60 | 220
F84ES | F96T12/ES | Fluorescent, (4) 96", ES lamp | Mag-STD | 4 | 60 | 276
F84EVS | F96T12/VHO/ES | Fluorescent, (4) 96", ES VHO lamp | Mag-STD | 4 | 185 | 780
F84ILL | F96T8 | Fluorescent, (4) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 59 | 219
F84LHL | F96T8/HO | Fluorescent, (4) 96", T8 HO lamp | Electronic | 4 | 86 | 320
F84SE | F96T12 | Fluorescent, (4) 96", STD lamp | Mag-ES | 4 | 75 | 316
F84SHE | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Mag-ES | 4 | 110 | 474
F84SHL | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Electronic | 4 | 110 | 390 | 2010-10-12 | Changed description from 3 lamp to 4 lamp
F84SHS | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Mag-STD | 4 | 110 | 514
F84SL | F96T12 | Fluorescent, (4) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 4 | 75 | 268
F84SS | F96T12 | Fluorescent, (4) 96", STD lamp | Mag-STD | 4 | 75 | 346
F84SVS | F96T12/VHO | Fluorescent, (4) 96", STD VHO lamp | Mag-STD | 4 | 215 | 900
F86EHS | F96T12/HO/ES | Fluorescent, (6) 96", ES HO lamp | Mag-STD | 6 | 95 | 721
F86ILL | F96T8 | Fluorescent, (6) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 6 | 59 | 328
F86EE | F96T12/ES | Fluorescent, (6) 96", ES lamp | Mag-ES | 6 | 60 | 369 | 2010-03-18 | New Code - F82EE + F84EE
F86EL | F96T12/ES | Fluorescent, (6) 96", ES lamp | Electronic | 6 | 60 | 330 | 2010-03-18 | New Code - F82EL + F84EL
Circline Fluorescent Fixtures
FC12/1 | FC12T9 | Fluorescent, (1) 12" circular lamp, RS ballast | Mag-STD | 1 | 32 | 31
FC12/2 | FC12T9 | Fluorescent, (2) 12" circular lamp, RS ballast | Mag-STD | 2 | 32 | 62
FC16/1 | FC16T9 | Fluorescent, (1) 16" circular lamp | Mag-STD | 1 | 40 | 35
FC20 | FC6T9 | Fluorescent, Circlite, (1) 20W lamp, Preheat ballast | Mag-STD | 1 | 20 | 20
FC22/1 | FC8T9 | Fluorescent, Circlite, (1) 22W lamp, preheat ballast | Mag-STD | 1 | 22 | 20
FC22/32/1 | FC22/32T9 | Fluorescent, Circlite, (1) 22W/32W lamp, preheat ballast | Mag-STD | 1 | 22/32 | 58
FC32/1 | FC12T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD | 1 | 32 | 40
FC32/40/1 | FC32/40T9 | Fluorescent, Circlite, (1) 32W/40W lamp, preheat ballast | Mag-STD | 1 | 32/40 | 80
FC40/1 | FC16T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD | 1 | 32 | 42
FC44/1 | FC44T9 | Fluorescent, Circlite, (1) 44W lamp, preheat ballast | Mag-STD | 1 | 44 | 46
FC6/1 | FC6T9 | Fluorescent, (1) 6" circular lamp, RS ballast | Mag-STD | 1 | 20 | 25
FC8/1 | FC8T9 | Fluorescent, (1) 8" circular lamp, RS ballast | Mag-STD | 1 | 22 | 26
FC8/2 | FC8T9 | Fluorescent, (2) 8" circular lamp, RS ballast | Mag-STD | 2 | 22 | 52
U-Tube Fluorescent Fixtures
FU1EE | FU40T12/ES | Fluorescent, (1) U-Tube, ES lamp | Mag-ES | 1 | 34 | 43
FU1ILL | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, Instant Start ballast | Electronic | 1 | 32 | 31
FU1LL | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp | Electronic | 1 | 32 | 32
FU1LL-R | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, RLO (BF<0.85) | Electronic | 1 | 31 | 27
FU2SS | FU40T12 | Fluorescent, (2) U-Tube, STD lamp | Mag-STD | 2 | 40 | 96
FU2SE | FU40T12 | Fluorescent, (2) U-Tube, STD lamp | Mag-ES | 2 | 40 | 85
FU2EE | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamp | Mag-ES | 2 | 34 | 72
FU2ES | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamp | Mag-STD | 2 | 34 | 82
FU2ILL | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast | Electronic | 2 | 32 | 59
FU2ILL/T4 | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast, tandem wired | Electronic | 2 | 32 | 56
FU2ILL/T4-R | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast, RLO, tandem wired | Electronic | 2 | 32 | 51
FU2ILL-H | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start HLO Ballast | Electronic | 2 | 32 | 65
FU2ILL-R | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start RLO Ballast | Electronic | 2 | 32 | 52
FU2LL | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp | Electronic | 2 | 32 | 60
FU2LL/T2 | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Tandem 4 lamp ballast | Electronic | 2 | 32 | 59
FU2LL-R | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, RLO (BF<0.85) | Electronic | 2 | 31 | 54 | 2010-10-12 | Changed lamp/fixture from 54 to 2
FU3EE | FU40T12/ES | Fluorescent, (3) U-Tube, ES lamp | Mag-ES | 3 | 35 | 115
FU3ILL | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamp, Instant Start Ballast | Electronic | 3 | 32 | 89
FU3ILL-R | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamp, Instant Start RLO Ballast | Electronic | 3 | 32 | 78
Standard Incandescent Fixtures
I100/1 | I100 | Incandescent, (1) 100W lamp |  | 1 | 100 | 100
I100/2 | I100 | Incandescent, (2) 100W lamp |  | 2 | 100 | 200
I100/3 | I100 | Incandescent, (3) 100W lamp |  | 3 | 100 | 300
I100/4 | I100 | Incandescent, (4) 100W lamp |  | 4 | 100 | 400
I100/5 | I100 | Incandescent, (5) 100W lamp |  | 5 | 100 | 500
I1000/1 | I1000 | Incandescent, (1) 1000W lamp |  | 1 | 1000 | 1000
I100E/1 | I100/ES | Incandescent, (1) 100W ES lamp |  | 1 | 90 | 90
I100EL/1 | I100/ES/LL | Incandescent, (1) 100W ES/LL lamp |  | 1 | 90 | 90
I120/1 | I120 | Incandescent, (1) 120W lamp |  | 1 | 120 | 120
I120/2 | I120 | Incandescent, (2) 120W lamp |  | 2 | 120 | 240
I125/1 | I125 | Incandescent, (1) 125W lamp |  | 1 | 125 | 125
I135/1 | I135 | Incandescent, (1) 135W lamp |  | 1 | 135 | 135
I135/2 | I135 | Incandescent, (2) 135W lamp |  | 2 | 135 | 270
I15/1 | I15 | Incandescent, (1) 15W lamp |  | 1 | 15 | 15
I15/2 | I15 | Incandescent, (2) 15W lamp |  | 2 | 15 | 30
I150/1 | I150 | Incandescent, (1) 150W lamp |  | 1 | 150 | 150
I150/2 | I150 | Incandescent, (2) 150W lamp |  | 2 | 150 | 300
I1500/1 | I1500 | Incandescent, (1) 1500W lamp |  | 1 | 1500 | 1500
I150E/1 | I150/ES | Incandescent, (1) 150W ES lamp |  | 1 | 135 | 135
I150EL/1 | I150/ES/LL | Incandescent, (1) 150W ES/LL lamp |  | 1 | 135 | 135
I170/1 | I170 | Incandescent, (1) 170W lamp |  | 1 | 170 | 170
I20/1 | I20 | Incandescent, (1) 20W lamp |  | 1 | 20 | 20
I20/2 | I20 | Incandescent, (2) 20W lamp |  | 2 | 20 | 40
I200/1 | I200 | Incandescent, (1) 200W lamp |  | 1 | 200 | 200
I200/2 | I200 | Incandescent, (2) 200W lamp |  | 2 | 200 | 400
I2000/1 | I2000 | Incandescent, (1) 2000W lamp |  | 1 | 2000 | 2000
I200L/1 | I200/LL | Incandescent, (1) 200W LL lamp |  | 1 | 200 | 200
I25/1 | I25 | Incandescent, (1) 25W lamp |  | 1 | 25 | 25
I25/2 | I25 | Incandescent, (2) 25W lamp |  | 2 | 25 | 50
I25/4 | I25 | Incandescent, (4) 25W lamp |  | 4 | 25 | 100
I250/1 | I250 | Incandescent, (1) 250W lamp |  | 1 | 250 | 250
I300/1 | I300 | Incandescent, (1) 300W lamp |  | 1 | 300 | 300
I34/1 | I34 | Incandescent, (1) 34W lamp |  | 1 | 34 | 34
I34/2 | I34 | Incandescent, (2) 34W lamp |  | 2 | 34 | 68
I36/1 | I36 | Incandescent, (1) 36W lamp |  | 1 | 36 | 36
I40/1 | I40 | Incandescent, (1) 40W lamp |  | 1 | 40 | 40
I40/2 | I40 | Incandescent, (2) 40W lamp |  | 2 | 40 | 80
I400/1 | I400 | Incandescent, (1) 400W lamp |  | 1 | 400 | 400
I40E/1 | I40/ES | Incandescent, (1) 40W ES lamp |  | 1 | 34 | 34
I40EL/1 | I40/ES/LL | Incandescent, (1) 40W ES/LL lamp |  | 1 | 34 | 34
I42/1 | I42 | Incandescent, (1) 42W lamp |  | 1 | 42 | 42
I448/1 | I448 | Incandescent, (1) 448W lamp |  | 1 | 448 | 448
I45/1 | I45 | Incandescent, (1) 45W lamp |  | 1 | 45 | 45
I50/1 | I50 | Incandescent, (1) 50W lamp |  | 1 | 50 | 50
I50/2 | I50 | Incandescent, (2) 50W lamp |  | 2 | 50 | 100
I500/1 | I500 | Incandescent, (1) 500W lamp |  | 1 | 500 | 500
I52/1 | I52 | Incandescent, (1) 52W lamp |  | 1 | 52 | 52
I52/2 | I52 | Incandescent, (2) 52W lamp |  | 2 | 52 | 104
I54/1 | I54 | Incandescent, (1) 54W lamp |  | 1 | 54 | 54
I54/2 | I54 | Incandescent, (2) 54W lamp |  | 2 | 54 | 108
I55/1 | I55 | Incandescent, (1) 55W lamp |  | 1 | 55 | 55
I55/2 | I55 | Incandescent, (2) 55W lamp |  | 2 | 55 | 110
I60/1 | I60 | Incandescent, (1) 60W lamp |  | 1 | 60 | 60
I60/2 | I60 | Incandescent, (2) 60W lamp |  | 2 | 60 | 120
I60/3 | I60 | Incandescent, (3) 60W lamp |  | 3 | 60 | 180
I60/4 | I60 | Incandescent, (4) 60W lamp |  | 4 | 60 | 240
I60/5 | I60 | Incandescent, (5) 60W lamp |  | 5 | 60 | 300
I60E/1 | I60/ES | Incandescent, (1) 60W ES lamp |  | 1 | 52 | 52
I60EL/1 | I60/ES/LL | Incandescent, (1) 60W ES/LL lamp |  | 1 | 52 | 52
I65/1 | I65 | Incandescent, (1) 65W lamp |  | 1 | 65 | 65
I65/2 | I65 | Incandescent, (2) 65W lamp |  | 2 | 65 | 130
I67/1 | I67 | Incandescent, (1) 67W lamp |  | 1 | 67 | 67
I67/2 | I67 | Incandescent, (2) 67W lamp |  | 2 | 67 | 134
I67/3 | I67 | Incandescent, (3) 67W lamp |  | 3 | 67 | 201
I69/1 | I69 | Incandescent, (1) 69W lamp |  | 1 | 69 | 69
I7.5/1 | I7.5 | Tungsten exit light, (1) 7.5 W lamp, used in night light application |  | 1 | 7.5 | 8
I7.5/2 | I7.5 | Tungsten exit light, (2) 7.5 W lamp, used in night light application |  | 2 | 7.5 | 15
I72/1 | I72 | Incandescent, (1) 72W lamp |  | 1 | 72 | 72
I75/1 | I75 | Incandescent, (1) 75W lamp |  | 1 | 75 | 75
I75/2 | I75 | Incandescent, (2) 75W lamp |  | 2 | 75 | 150
I75/3 | I75 | Incandescent, (3) 75W lamp |  | 3 | 75 | 225
I75/4 | I75 | Incandescent, (4) 75W lamp |  | 4 | 75 | 300
I750/1 | I750 | Incandescent, (1) 750W lamp |  | 1 | 750 | 750
I75E/1 | I75/ES | Incandescent, (1) 75W ES lamp |  | 1 | 67 | 67
I75EL/1 | I75/ES/LL | Incandescent, (1) 75W ES/LL lamp |  | 1 | 67 | 67
I80/1 | I80 | Incandescent, (1) 80W lamp |  | 1 | 80 | 80
I85/1 | I85 | Incandescent, (1) 85W lamp |  | 1 | 85 | 85
I90/1 | I90 | Incandescent, (1) 90W lamp |  | 1 | 90 | 90
I90/2 | I90 | Incandescent, (2) 90W lamp |  | 2 | 90 | 180
I90/3 | I90 | Incandescent, (3) 90W lamp |  | 3 | 90 | 270
I93/1 | I93 | Incandescent, (1) 93W lamp |  | 1 | 93 | 93
I95/1 | I95 | Incandescent, (1) 95W lamp |  | 1 | 95 | 95
I95/2 | I95 | Incandescent, (2) 95W lamp |  | 2 | 95 | 190
Halogen Incandescent Fixtures
H100/1 | H100 | Halogen Incandescent, (1) 100W lamp |  | 1 | 100 | 100
H1000/1 | H1000 | Halogen Incandescent, (1) 1000W lamp |  | 1 | 1000 | 1000
H1200/1 | H1200 | Halogen Incandescent, (1) 1200W lamp |  | 1 | 1200 | 1200
H150/1 | H150 | Halogen Incandescent, (1) 150W lamp |  | 1 | 150 | 150
H150/2 | H150 | Halogen Incandescent, (2) 150W lamp |  | 2 | 150 | 300
H1500/1 | H1500 | Halogen Incandescent, (1) 1500W lamp |  | 1 | 1500 | 1500
H200/1 | H200 | Halogen Incandescent, (1) 200W lamp |  | 1 | 200 | 200
H250/1 | H250 | Halogen Incandescent, (1) 250W lamp |  | 1 | 250 | 250
H300/1 | H300 | Halogen Incandescent, (1) 300W lamp |  | 1 | 300 | 300
H35/1 | H35 | Halogen Incandescent, (1) 35W lamp |  | 1 | 35 | 35
H350/1 | H350 | Halogen Incandescent, (1) 350W lamp |  | 1 | 350 | 350
H40/1 | H40 | Halogen Incandescent, (1) 40W lamp |  | 1 | 40 | 40
H400/1 | H400 | Halogen Incandescent, (1) 400W lamp |  | 1 | 400 | 400
H42/1 | H42 | Halogen Incandescent, (1) 42W lamp |  | 1 | 42 | 42
H425/1 | H425 | Halogen Incandescent, (1) 425W lamp |  | 1 | 425 | 425
H45/1 | H45 | Halogen Incandescent, (1) 45W lamp |  | 1 | 45 | 45
H45/2 | H45 | Halogen Incandescent, (2) 45W lamp |  | 2 | 45 | 90
H50/1 | H50 | Halogen Incandescent, (1) 50W lamp |  | 1 | 50 | 50
H50/2 | H50 | Halogen Incandescent, (2) 50W lamp |  | 2 | 50 | 100
H500/1 | H500 | Halogen Incandescent, (1) 500W lamp |  | 1 | 500 | 500
H52/1 | H52 | Halogen Incandescent, (1) 52W lamp |  | 1 | 52 | 52
H55/1 | H55 | Halogen Incandescent, (1) 55W lamp |  | 1 | 55 | 55
H55/2 | H55 | Halogen Incandescent, (2) 55W lamp |  | 2 | 55 | 110
H60/1 | H60 | Halogen Incandescent, (1) 60W lamp |  | 1 | 60 | 60
H72/1 | H72 | Halogen Incandescent, (1) 72W lamp |  | 1 | 72 | 72
H75/1 | H75 | Halogen Incandescent, (1) 75W lamp |  | 1 | 75 | 75
H75/2 | H75 | Halogen Incandescent, (2) 75W lamp |  | 2 | 75 | 150
H750/1 | H750 | Halogen Incandescent, (1) 750W lamp |  | 1 | 750 | 750
H90/1 | H90 | Halogen Incandescent, (1) 90W lamp |  | 1 | 90 | 90
H90/2 | H90 | Halogen Incandescent, (2) 90W lamp |  | 2 | 90 | 180
H900/1 | H900 | Halogen Incandescent, (1) 900W lamp |  | 1 | 900 | 900
HLV20/1 | H20/LV | Halogen Low Voltage Incandescent, (1) 20W lamp |  | 1 | 20 | 30
HLV25/1 | H25/LV | Halogen Low Voltage Incandescent, (1) 25W lamp |  | 1 | 25 | 35
HLV35/1 | H35/LV | Halogen Low Voltage Incandescent, (1) 35W lamp |  | 1 | 35 | 45
HLV42/1 | H42/LV | Halogen Low Voltage Incandescent, (1) 42W lamp |  | 1 | 42 | 52
HLV50/1 | H50/LV | Halogen Low Voltage Incandescent, (1) 50W lamp |  | 1 | 50 | 60
HLV65/1 | H65/LV | Halogen Low Voltage Incandescent, (1) 65W lamp |  | 1 | 65 | 75
HLV75/1 | H75/LV | Halogen Low Voltage Incandescent, (1) 75W lamp |  | 1 | 75 | 85
QL Induction Fixtures
QL55/1 | QL55 | QL Induction, (1) 55W lamp | Generator | 1 | 55 | 55
QL85/1 | QL85 | QL Induction, (1) 85W lamp | Generator | 1 | 85 | 85
QL165/1 | QL165 | QL Induction, (1) 165W lamp | Generator | 1 | 165 | 165
High Pressure Sodium Fixtures
HPS100/1 | HPS100 | High Pressure Sodium, (1) 100W lamp | CWA | 1 | 100 | 138
HPS1000/1 | HPS1000 | High Pressure Sodium, (1) 1000W lamp | CWA | 1 | 1000 | 1100
HPS150/1 | HPS150 | High Pressure Sodium, (1) 150W lamp | CWA | 1 | 150 | 188
HPS200/1 | HPS200 | High Pressure Sodium, (1) 200W lamp | CWA | 1 | 200 | 250
HPS225/1 | HPS225 | High Pressure Sodium, (1) 225W lamp | CWA | 1 | 225 | 275
HPS250/1 | HPS250 | High Pressure Sodium, (1) 250W lamp | CWA | 1 | 250 | 295
HPS310/1 | HPS310 | High Pressure Sodium, (1) 310W lamp | CWA | 1 | 310 | 365
HPS35/1 | HPS35 | High Pressure Sodium, (1) 35W lamp | CWA | 1 | 35 | 46
HPS360/1 | HPS360 | High Pressure Sodium, (1) 360W lamp | CWA | 1 | 360 | 414
HPS400/1 | HPS400 | High Pressure Sodium, (1) 400W lamp | CWA | 1 | 400 | 465
HPS50/1 | HPS50 | High Pressure Sodium, (1) 50W lamp | CWA | 1 | 50 | 66
HPS600/1 | HPS600 | High Pressure Sodium, (1) 600W lamp | CWA | 1 | 600 | 675
HPS70/1 | HPS70 | High Pressure Sodium, (1) 70W lamp | CWA | 1 | 70 | 95
HPS750/1 | HPS750 | High Pressure Sodium, (1) 750W lamp | CWA | 1 | 750 | 835
Metal Halide Fixtures
MH100/1 | MH100 | Metal Halide, (1) 100W lamp | CWA | 1 | 100 | 128
MH1000/1 | MH1000 | Metal Halide, (1) 1000W lamp | CWA | 1 | 1000 | 1080
MH150/1 | MH150 | Metal Halide, (1) 150W lamp | CWA | 1 | 150 | 190
MH1500/1 | MH1500 | Metal Halide, (1) 1500W lamp | CWA | 1 | 1500 | 1610
MH175/1 | MH175 | Metal Halide, (1) 175W lamp | CWA | 1 | 175 | 215
MH1800/1 | MH1800 | Metal Halide, (1) 1800W lamp | CWA | 1 | 1800 | 1875
MH200/1 | MH200 | Metal Halide, (1) 200W lamp | CWA | 1 | 200 | 232
MH250/1 | MH250 | Metal Halide, (1) 250W lamp | CWA | 1 | 250 | 295
MH32/1 | MH32 | Metal Halide, (1) 32W lamp | CWA | 1 | 32 | 43
MH300/1 | MH300 | Metal Halide, (1) 300W lamp | CWA | 1 | 300 | 342
MH320/1 | MH320 | Metal Halide, (1) 320W lamp | CWA | 1 | 320 | 365
MH350/1 | MH350 | Metal Halide, (1) 350W lamp | CWA | 1 | 350 | 400
MH360/1 | MH360 | Metal Halide, (1) 360W lamp | CWA | 1 | 360 | 430
MH400/1 | MH400 | Metal Halide, (1) 400W lamp | CWA | 1 | 400 | 458
MH400/2 | MH400 | Metal Halide, (2) 400W lamp | CWA | 2 | 400 | 916
MH450/1 | MH450 | Metal Halide, (1) 450W lamp | CWA | 1 | 450 | 508
MH35/1 | MH35 | Metal Halide, (1) 35W lamp | CWA | 1 | 35 | 44
MH50/1 | MH50 | Metal Halide, (1) 50W lamp | CWA | 1 | 50 | 72
MH70/1 | MH70 | Metal Halide, (1) 70W lamp | CWA | 1 | 70 | 95
MH750/1 | MH750 | Metal Halide, (1) 750W lamp | CWA | 1 | 750 | 850
MHPS/LR/100/1 | MHPS100 | Metal Halide Pulse Start, (1) 100W lamp w/ Linear Reactor Ballast | LR | 1 | 100 | 118
MHPS/LR/150/1 | MHPS150 | Metal Halide Pulse Start, (1) 150W lamp w/ Linear Reactor Ballast | LR | 1 | 150 | 170
MHPS/LR/175/1 | MHPS175 | Metal Halide Pulse Start, (1) 175W lamp w/ Linear Reactor Ballast | LR | 1 | 175 | 194
MHPS/LR/200/1 | MHPS200 | Metal Halide Pulse Start, (1) 200W lamp w/ Linear Reactor Ballast | LR | 1 | 200 | 219
MHPS/LR/250/1 | MHPS250 | Metal Halide Pulse Start, (1) 250W lamp w/ Linear Reactor Ballast | LR | 1 | 250 | 275
MHPS/LR/300/1 | MHPS300 | Metal Halide Pulse Start, (1) 300W lamp w/ Linear Reactor Ballast | LR | 1 | 300 | 324
MHPS/LR/320/1 | MHPS320 | Metal Halide Pulse Start, (1) 320W lamp w/ Linear Reactor Ballast | LR | 1 | 320 | 349
MHPS/LR/350/1 | MHPS350 | Metal Halide Pulse Start, (1) 350W lamp w/ Linear Reactor Ballast | LR | 1 | 350 | 380
MHPS/LR/400/1 | MHPS400 | Metal Halide Pulse Start, (1) 400W lamp w/ Linear Reactor Ballast | LR | 1 | 400 | 435
MHPS/LR/450/1 | MHPS450 | Metal Halide Pulse Start, (1) 450W lamp w/ Linear Reactor Ballast | LR | 1 | 450 | 485
MHPS/LR/750/1 | MHPS750 | Metal Halide Pulse Start, (1) 750W lamp w/ Linear Reactor Ballast | LR | 1 | 750 | 805
MHPS/SCWA/100/1 | MHPS100 | Metal Halide Pulse Start, (1) 100W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 100 | 128
MHPS/SCWA/1000/1 | MHPS1000 | Metal Halide Pulse Start, (1) 1000W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 1000 | 1080
MHPS/SCWA/150/1 | MHPS150 | Metal Halide Pulse Start, (1) 150W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 150 | 190
MHPS/SCWA/175/1 | MHPS175 | Metal Halide Pulse Start, (1) 175W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 175 | 208
MHPS/SCWA/200/1 | MHPS200 | Metal Halide Pulse Start, (1) 200W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 200 | 232
MHPS/SCWA/250/1 | MHPS250 | Metal Halide Pulse Start, (1) 250W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 250 | 288
MHPS/SCWA/300/1 | MHPS300 | Metal Halide Pulse Start, (1) 300W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 300 | 342
MHPS/SCWA/320/1 | MHPS320 | Metal Halide Pulse Start, (1) 320W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 320 | 368
MHPS/SCWA/350/1 | MHPS350 | Metal Halide Pulse Start, (1) 350W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 350 | 400
MHPS/SCWA/400/1 | MHPS400 | Metal Halide Pulse Start, (1) 400W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 400 | 450
MHPS/SCWA/450/1 | MHPS450 | Metal Halide Pulse Start, (1) 450W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 450 | 506
MHPS/SCWA/750/1 | MHPS750 | Metal Halide Pulse Start, (1) 750W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 | 750 | 815
Mercury Vapor Fixtures
MV100/1 | MV100 | Mercury Vapor, (1) 100W lamp | CWA | 1 | 100 | 125
MV1000/1 | MV1000 | Mercury Vapor, (1) 1000W lamp | CWA | 1 | 1000 | 1075
MV175/1 | MV175 | Mercury Vapor, (1) 175W lamp | CWA | 1 | 175 | 205
MV250/1 | MV250 | Mercury Vapor, (1) 250W lamp | CWA | 1 | 250 | 290
MV40/1 | MV40 | Mercury Vapor, (1) 40W lamp | CWA | 1 | 40 | 50
MV400/1 | MV400 | Mercury Vapor, (1) 400W lamp | CWA | 1 | 400 | 455
MV400/2 | MV400 | Mercury Vapor, (2) 400W lamp | CWA | 2 | 400 | 910
MV50/1 | MV50 | Mercury Vapor, (1) 50W lamp | CWA | 1 | 50 | 74
MV700/1 | MV700 | Mercury Vapor, (1) 700W lamp | CWA | 1 | 700 | 780
MV75/1 | MV75 | Mercury Vapor, (1) 75W lamp | CWA | 1 | 75 | 93
Miscellaneous
N/A | N/A | N/A | N/A | N/A | N/A | N/A
Add | None | This pre-fixture code should be used as a placeholder when adding new additional fixtures. |  | 0 | 0 | 0
Removed | None | This post-fixture code should be used when the fixture(s) is(are) completely removed from service. |  | 0 | 0 | 0
Cut Sheet Fixtures
Cut Sheet 1 |  | Edit |  |  |  | Edit
Cut Sheet 2 |  | Edit |  |  |  | Edit
Cut Sheet 3 |  | Edit |  |  |  | Edit
Cut Sheet 4 |  | Edit |  |  |  | Edit
Cut Sheet 5 |  | Edit |  |  |  | Edit
Cut Sheet 6 |  | Edit |  |  |  | Edit
Cut Sheet 7 |  | Edit |  |  |  | Edit
Cut Sheet 8 |  | Edit |  |  |  | Edit
Cut Sheet 9 |  | Edit |  |  |  | Edit
Cut Sheet 10 |  | Edit |  |  |  | Edit
Cut Sheet 11 |  | Edit |  |  |  | Edit
Cut Sheet 12 |  | Edit |  |  |  | Edit
Cut Sheet 13 |  | Edit |  |  |  | Edit
Cut Sheet 14 |  | Edit |  |  |  | Edit
Cut Sheet 15 |  | Edit |  |  |  | Edit
Cut Sheet 16 |  | Edit |  |  |  | Edit
Cut Sheet 17 |  | Edit |  |  |  | Edit
Cut Sheet 18 |  | Edit |  |  |  | Edit
Cut Sheet 19 |  | Edit |  |  |  | Edit
Cut Sheet 20 |  | Edit |  |  |  | Edit
Cut Sheet 21 |  | Edit |  |  |  | Edit
Cut Sheet 22 |  | Edit |  |  |  | Edit
Cut Sheet 23 |  | Edit |  |  |  | Edit
Cut Sheet 24 |  | Edit |  |  |  | Edit
Cut Sheet 25 |  | Edit |  |  |  | Edit
Cut Sheet 26 |  | Edit |  |  |  | Edit
Cut Sheet 27 |  | Edit |  |  |  | Edit
Cut Sheet 28 |  | Edit |  |  |  | Edit
Cut Sheet 29 |  | Edit |  |  |  | Edit
Cut Sheet 30 |  | Edit |  |  |  | Edit
Cut Sheet 31 |  | Edit |  |  |  | Edit
Cut Sheet 32 |  | Edit |  |  |  | Edit
Cut Sheet 33 |  | Edit |  |  |  | Edit
Cut Sheet 34 |  | Edit |  |  |  | Edit
Cut Sheet 35 |  | Edit |  |  |  | Edit
Cut Sheet 36 |  | Edit |  |  |  | Edit
Cut Sheet 37 |  | Edit |  |  |  | Edit
Cut Sheet 38 |  | Edit |  |  |  | Edit
Cut Sheet 39 |  | Edit |  |  |  | Edit
Cut Sheet 40 |  | Edit |  |  |  | Edit
Cut Sheet 41 |  | Edit |  |  |  | Edit
Cut Sheet 42 |  | Edit |  |  |  | Edit
Cut Sheet 43 |  | Edit |  |  |  | Edit
Cut Sheet 44 |  | Edit |  |  |  | Edit
Cut Sheet 45 |  | Edit |  |  |  | Edit
Cut Sheet 46 |  | Edit |  |  |  | Edit
Cut Sheet 47 |  | Edit |  |  |  | Edit
Cut Sheet 48 |  | Edit |  |  |  | Edit
Cut Sheet 49 |  | Edit |  |  |  | Edit
Cut Sheet 50 |  | Edit |  |  |  | Edit

## Fixture Code Legend
Fixture Code Legend and Notes
Sample Linear Fluorescent Fixture Code |  |  |  | Sample of Other Fixture Code:
|  | CONFIGURATION (letter) |  | FIXTURE TYPE |  |  | NUMBER OF LAMPS
NUMBER OF LAMPS |  | Tandem Wired |  | Compact Fluorescent, |  |  | 1 Lamp Fixture
|  |  | CONFIGURATION (number) | Quad Tube
FIXTURE TYPE |  |  | 4 Lamps on this Ballast
Fluorescent | [5 empty] | CFQ18/1-L
F41ILL/T4-R
BALLAST LIGHT OUTPUT
LAMP LENGTH |  |  | Reduced Light Output | NATIONAL LAMP WATTAGE |  |  | BALLAST TYPE
4 Feet |  |  |  |  | 18W |  | Electronic Ballast
| LAMP TYPE |  | BALLAST TYPE
| Instant start, T8 |  | Electronic Ballast
Code Explanations
Fixture Type |  |  |  | for LED traffic signals
CF | Compact Fluorescent
CFD | Compact Fluorescent, double-D shape |  |  | 12GA | 12" Green Arrow
CFS | Compact Fluorescent, Spiral |  |  | 12GB | 12" Green Ball
CFT | Compact Fluorescent, Twin tube |  |  | 12RA | 12" Red Arrow
| (including "Biaxial" fixtures) |  |  | 12RB | 12" Red Ball
CFQ | Compact Fluorescent, Quad tube |  |  | 8GB | 8" Green Ball
ECF | Exit sign, Compact Fluorescent |  |  | 8RB | 8" Red Ball
EI | Exit sign, Incandescent |  |  | PH | Pedestrian Hand signal
ELED | Exit sign, LED
F | Fluorescent, linear |  |  | Ballast Type
FC | Fluorescent, Circline |  |  | for fluorescent fixtures
FU | Fluorescent, U-tube |  |  | L | Electronic
H | Halogen |  |  | S | Standard magnetic
HLV | Halogen, Low Voltage |  |  | E | Emergy efficient magnetic
HPS | High Pressure Sodium
I | Incandescent |  |  | Configuration (letter)
LED | Light Emitting Diode (LED) traffic signal |  |  | T | Tandem wired fixture
MH | Metal Halide |  |  | D | Delamped fixture, i.e. some lamps
MHPS | Metal Halide, Pulse Start |  |  |  | permanently removed but ballasts
MV | Mercury Vapor |  |  |  | remain
QL | Induction
Configuration (number)
Lamp Type |  |  |  | for delamped fixtures
for fluorescent fixtures |  |  |  | Number signifies the total number of ballasts
A | "F25T12" - 25 watt, 4ft, T12 lamp |  |  | in the fixture: e.g. An "F42EEID2" is an
IL | T8, Instant start |  |  | "F44EE" with two lamps removed so that there
SIL | T8, Instant start, Super 30 watt |  |  | is one extaneous ballast
SSIL | T8, Instant start, Super 28 watt
L | T8, rapid start |  |  | for tandem wired ballasts
G | T5, standard |  |  | Number signifies the total number of lamps
GH | T5, standard, High output lamp |  |  | being run by the ballast: e.g. An "F42LLIT4"
E | T12, Energy efficient |  |  | would indicate that a four-lamp ballast is
EH | T12, Energy efficient, High output lamp |  |  | wired to run two-lamp fixtures.
EI | T12, Energy efficient, Instant start
EV | T12, Energy efficient, Very high output |  |  | with no preceding letter
S | T12, Standard |  |  | Number indicates the number of ballasts in an
SIL | T12, Standard, Instant start |  |  | ambiguous multiple ballast fixture: e.g. An
SH | T12, Standard, High output lamp |  |  | "F43ILU2" indicates a three-lamp fixture with
SV | T12, Standard, Very high output lamp |  |  | two ballasts (as is often the case if there is A/B
T | T10, Standard |  |  | switching).
Ballast Light Output
|  |  |  | R | Reduced light output
|  |  |  | H | High light output
|  |  |  | V | Very high light output
Notes:
1) The column labeled Watts/Fixtures in the data table includes ballast loads.
2) The fixture wattage values represent an average value, rounded to the nearest whole watt.

## Fixture Code Locator
Pennsylvania Act 129 Lighting Audit and Design Tool
LIGHTING FIXTURE CODE LOCATOR | [14 empty] | Password: Act129Lighting
*Required | Fill In Tan Fields
**Required for all except U-Tube |  |  | SELECTED | [5 empty] | FIXTURE TYPE |  |  |  | LAMP TYPE |  | CONFIGURATION (NUMBER)
Linear Fluorescent Fixtures Only |  |  | Compact Fluorescent | Standard | Double-D shape | Spiral | Twin tube (including "Biaxial") | Quad tube | Compact Fluorescent | Standard | Compact FluorescentStandard | CF | T5, Standard | G | for delamped fixtures
|  |  | Fluorescent | Circline | U-Tube |  |  |  | Compact Fluorescent | Double-D shape | Compact FluorescentDouble-D shape | CFD | T5, Standard, High output lamp | GH | Number signifies the total number of ballasts
Fixture Type*: | Fluorescent |  | Halogen | Standard | Low Voltage |  |  |  | Compact Fluorescent | Spiral | Compact FluorescentSpiral | CFS | T8, Instant Start | IL | in the fixture: e.g. An "F42EEID2" is an
Fixture Subtype*: | Linear | F | High Pressure Sodium | Standard |  |  |  |  | Compact Fluorescent | Twin tube (including "Biaxial") | Compact FluorescentTwin tube (including "Biaxial") | CFT | T8, Instant Start, Super 30 watt | SIL | "F44EE" with two lamps removed so that there
Lamp Length*: |  |  | Incandescent | Standard |  |  |  |  | Compact Fluorescent | Quad tube | Compact FluorescentQuad tube | CFQ | T8, Instant Start, Super 28 watt | SSIL | is one extaneous ballast
Number of Lamps*: |  |  | Induction | Standard |  |  |  |  | Exit Sign | Compact Fluorescent | Exit SignCompact Fluorescent | ECF | T8, Rapid Start | L
Lamp Type*: |  |  | Metal Halide | Standard | Pulse Start |  |  |  | Exit Sign | Incandescent | Exit SignIncandescent | EI | T10, Standard | T | for tandem wired ballasts
Ballast Type*: |  |  | Mercury Vapor | Standard |  |  |  |  | Exit Sign | LED | Exit SignLED | ELED | T12, Energy Efficient | E | Number signifies the total number of lamps
Configuration (Letter): |  |  | Exit Sign | Compact Fluorescent | Incandescent | LED |  |  | Fluorescent | Linear | FluorescentLinear | F | T12, Energy Efficient, High output lamp | EH | being run by the ballast: e.g. An "F42LLIT4"
Configuration (Number): |  |  | Traffic Signal LED | 12" Green Arrow | 12" Green Ball | 12" Red Arrow | 12" Red Ball | Pedestrian Hand signal | Fluorescent | Circline | FluorescentCircline | FC | T12, Energy Efficient, Instant start | EI | would indicate that a four-lamp ballast is
Ballast Light Output: | [8 empty] | Fluorescent | U-Tube | FluorescentU-Tube | FU | T12, Energy Efficient, Very high output | EV | wired to run two-lamp fixtures.
|  |  | BALLAST TYPE | [5 empty] | Halogen | Standard | HalogenStandard | H | T12, Standard | S
Fixture Code: | Fill In All Applicable Fields | F | Electronic | L |  |  |  |  | Halogen | Low Voltage | HalogenLow Voltage | HLV | T12, Standard, Instant start | SIL | with no preceding letter
|  |  | Standard Magnetic | S |  |  |  |  | High Pressure Sodium | Standard | High Pressure SodiumStandard | HPS | T12, Standard, High output lamp | SH | Number indicates the number of ballasts in an
|  |  | Energy Efficient Magnetic | E |  |  |  |  | Incandescent | Standard | IncandescentStandard | I | T12, Standard, Very high output lamp | SV | ambiguous multiple ballast fixture: e.g. An
All Other Fixtures | [8 empty] | Traffic Signal | LED | Traffic SignalLED | LED |  |  | "F43ILU2" indicates a three-lamp fixture with
|  |  | BALLAST LIGHT OUTPUT | [5 empty] | Metal Halide | Standard | Metal HalideStandard | MH |  |  | two ballasts (as is often the case if there is A/B
Fixture Type*: |  |  | Reduced Light Output | -R |  |  |  |  | Metal Halide | Pulse Start | Metal HalidePulse Start | MHPS |  |  | switching).
Fixture Subtype*: |  |  | High Light Output | -H |  |  |  |  | Mercury Vapor | Standard | Mercury VaporStandard | MV
Nominal Lamp Wattage*: |  |  | Very High Light Output | -V |  |  |  |  | Induction | Standard | InductionStandard | QL |  |  | See "Fixture Code Legend" sheet for additional help.
Number of Lamps**: | [8 empty] | Traffic Signal LED | 12" Green Arrow | Traffic Signal LED12" Green Arrow | 12GA
Ballast Type: |  |  | LAMP LENGTH | [5 empty] | Traffic Signal LED | 12" Green Ball | Traffic Signal LED12" Green Ball | 12GB |  |  | Only fixture codes listed in the Standard Wattage Table will be located.
|  |  | 1.5 Feet (18 Inches) | 1.5 |  |  |  |  | Traffic Signal LED | 12" Red Arrow | Traffic Signal LED12" Red Arrow | 12RA
Fixture Code: | Fill In All Applicable Fields |  | 2' Feet (24 Inches) | 2 |  |  |  |  | Traffic Signal LED | 12" Red Ball | Traffic Signal LED12" Red Ball | 12RB
|  |  | 3' Feet (36 Inches) | 3 |  |  |  |  | Traffic Signal LED | Pedestrian Hand signal | Traffic Signal LEDPedestrian Hand signal | PH
|  |  | 4' Feet (48 Inches) | 4
Disclaimer: This fixture code locator is still in development. In some cases, the locator may note that the fixture cannot be found due to the use of non-standard and diverse notations for fixture codes. A manual search of the wattage table is recommended to double-check results. |  |  | 5' Feet (60 Inches) | 5
|  |  | 6' Feet (72 Inches) | 6
|  |  | 8' Feet (96 Inches) | 8
NUMBER OF LAMPS
|  |  | 1 Lamp | 1
|  |  | 2 Lamps | 2
|  |  | 3 Lamps | 3
|  |  | 4 Lamps | 4
|  |  | 5 Lamps | 5
|  |  | 6 Lamps | 6
|  |  | 7 Lamps | 7
|  |  | 8 Lamps | 8
CONFIGURATION (LETTER)
|  |  | Tandem Wired Fixture | T
|  |  | Delamped Fixture | D
Note on B25: Manually Enter Number (No Drop-Down)

## Prescriptive Table
Prescriptive Lighting Table
| POST-INSTALLATION |  |  | PRE-INSTALLATION
Line Item | Upgrade Fixture | Post Fixture Code [*3] | Post Watts / Fixture | Existing Fixture | Pre Fixture Code [*3] | Pre Watts / Fixture | Change in Connected Load (Watts) | Notes
T-8 Linear Fluorescent Upgrade (EE T-12 with EE Magnetic Ballast as Baseline)
1 | 17W T-8 2' 1L Electronic Ballast | F21ILL | 20 | 20W T-12 2' 1L EE Magnetic Ballast | F21SE | 26 | 6 | Baseline uses standard T-12 lamps, not EE lamps
2 | 17W T-8 2' 2L Electronic Ballast | F22ILL | 33 | 20W T-12 2' 2L EE Magnetic Ballast | F22SE | 51 | 18 | Baseline uses standard T-12 lamps, not EE lamps
3 | 17W T-8 2' 3L Electronic Ballast | F23ILL | 47 | 20W T-12 2' 3L EE Magnetic Ballast | F23SE | 77 | 30 | Baseline uses standard T-12 lamps, not EE lamps
4 | 17W T-8 2' 4L Electronic Ballast | F24ILL | 61 | 20W T-12 2' 4L EE Magnetic Ballast | F24SE | 102 | 41 | Baseline uses standard T-12 lamps, not EE lamps
5 | 25W T-8 3' 1L Electronic Ballast | F31ILL | 26 | 25W T-12 3' 1L EE Magnetic Ballast | F31EE | 38 | 12
6 | 25W T-8 3' 2L Electronic Ballast | F32ILL | 46 | 25W T-12 3' 2L EE Magnetic Ballast | F32EE | 66 | 20
7 | 25W T-8 3' 3L Electronic Ballast | F33ILL | 67 | 25W T-12 3' 3L EE Magnetic Ballast | F33EE | 104 | 37
8 | 25W T-8 3' 4L Electronic Ballast | F34ILL | 87 | 25W T-12 3' 4L EE Magnetic Ballast | F34EE | 132 | 45
9 | 32W T-8 4' 1L Electronic Ballast | F41ILL | 31 | 34W T-12 4' 1L EE Magnetic Ballast | F41EE | 43 | 12
10 | 32W T-8 4' 2L Electronic Ballast | F42ILL | 59 | 34W T-12 4' 2L EE Magnetic Ballast | F42EE | 72 | 13
11 | 32W T-8 4' 3L Electronic Ballast | F43ILL | 89 | 34W T-12 4' 3L EE Magnetic Ballast | F43EE | 115 | 26
12 | 32W T-8 4' 4L Electronic Ballast | F44ILL | 112 | 34W T-12 4' 4L EE Magnetic Ballast | F44EE | 144 | 32
13 | 32W T-8 4' 6L Electronic Ballast | F46ILL | 175 | 34W T-12 4' 6L EE Magnetic Ballast | F46EE | 216 | 41
14 | 32W T-8 4' 2L VHLO Electronic Ballast | F42ILL-V | 79 | 34W T-12 4' 4L EE Magnetic Ballast | F44EE | 144 | 65 | 2-Lamp Upgrade of a 4-Lamp Baseline
15 | 32W T-8 4' 4L RLO Electronic Ballast | F44ILL-R | 102 | 34W T-12 4' 4L EE Magnetic Ballast | F44EE | 144 | 42
16 | 30W Super T-8 4' 1L Electronic Ballast | F41SILL | 28 | 34W T-12 4' 1L EE Magnetic Ballast | F41EE | 43 | 15 | Upgrade Fixture uses 30W Super T-8 Lamps
17 | 30W Super T-8 4' 2L Electronic Ballast | F42SILL | 53 | 34W T-12 4' 2L EE Magnetic Ballast | F42EE | 72 | 19 | Upgrade Fixture uses 30W Super T-8 Lamps
18 | 30W Super T-8 4' 3L Electronic Ballast | F43SILL | 78 | 34W T-12 4' 3L EE Magnetic Ballast | F43EE | 115 | 37 | Upgrade Fixture uses 30W Super T-8 Lamps
19 | 30W Super T-8 4' 4L Electronic Ballast | F44SILL | 105 | 34W T-12 4' 4L EE Magnetic Ballast | F44EE | 144 | 39 | Upgrade Fixture uses 30W Super T-8 Lamps
20 | 28W Super T-8 4' 1L Electronic Ballast | F41SSILL | 26 | 34W T-12 4' 1L EE Magnetic Ballast | F41EE | 43 | 17 | Upgrade Fixture uses 28W Super T-8 Lamps
21 | 28W Super T-8 4' 2L Electronic Ballast | F42SSILL | 48 | 34W T-12 4' 2L EE Magnetic Ballast | F42EE | 72 | 24 | Upgrade Fixture uses 28W Super T-8 Lamps
22 | 28W Super T-8 4' 3L Electronic Ballast | F43SSILL | 72 | 34W T-12 4' 3L EE Magnetic Ballast | F43EE | 115 | 43 | Upgrade Fixture uses 28W Super T-8 Lamps
23 | 28W Super T-8 4' 4L Electronic Ballast | F44SSILL | 96 | 34W T-12 4' 4L EE Magnetic Ballast | F44EE | 144 | 48 | Upgrade Fixture uses 28W Super T-8 Lamps
24 | 59W T-8 8' 1L Electronic Ballast | F81ILL | 58 | 60W T-12 8' 1L EE Magnetic Ballast | F81EE | 61 | 3
25 | 59W T-8 8' 2L Electronic Ballast | F82ILL | 109 | 60W T-12 8' 2L EE Magnetic Ballast | F82EE | 123 | 14
26 | 59W T-8 8' 4L Electronic Ballast | F84ILL | 219 | 60W T-12 8' 4L EE Magnetic Ballast | F84EE | 246 | 27
27 | 59W T-8 8' 6L Electronic Ballast | F86ILL | 328 | 60W T-12 8' 6L EE Magnetic Ballast | F86EE | 369 | 41
T-8 Linear Fluorescent Upgrade (EE T-12 with Electronic Ballast as Baseline)
28 | 17W T-8 2' 1L Electronic Ballast | F21ILL | 20 | N/A | N/A | N/A | N/A | Comparable baseline fixture using electronic ballast does not exist.
29 | 17W T-8 2' 2L Electronic Ballast | F22ILL | 33 | N/A | N/A | N/A | N/A | Comparable baseline fixture using electronic ballast does not exist.
30 | 17W T-8 2' 3L Electronic Ballast | F23ILL | 47 | N/A | N/A | N/A | N/A | Comparable baseline fixture using electronic ballast does not exist.
31 | 17W T-8 2' 4L Electronic Ballast | F24ILL | 61 | N/A | N/A | N/A | N/A | Comparable baseline fixture using electronic ballast does not exist.
32 | 25W T-8 3' 1L Electronic Ballast | F31ILL | 26 | 25W T-12 3' 1L Electronic Ballast | F31EL | 26 | 0
33 | 25W T-8 3' 2L Electronic Ballast | F32ILL | 46 | 25W T-12 3' 2L Electronic Ballast | F32EL | 50 | 4
34 | 25W T-8 3' 3L Electronic Ballast | F33ILL | 67 | 25W T-12 3' 3L Electronic Ballast | F33EL | 76 | 9
35 | 25W T-8 3' 4L Electronic Ballast | F34ILL | 87 | 25W T-12 3' 4L Electronic Ballast | F34EL | 100 | 13
36 | 32W T-8 4' 1L Electronic Ballast | F41ILL | 31 | 34W T-12 4' 1L Electronic Ballast | F41EL | 32 | 1
37 | 32W T-8 4' 2L Electronic Ballast | F42ILL | 59 | 34W T-12 4' 2L Electronic Ballast | F42EL | 60 | 1
38 | 32W T-8 4' 3L Electronic Ballast | F43ILL | 89 | 34W T-12 4' 3L Electronic Ballast | F43EL | 92 | 3
39 | 32W T-8 4' 4L Electronic Ballast | F44ILL | 112 | 34W T-12 4' 4L Electronic Ballast | F44EL | 120 | 8
40 | 32W T-8 4' 6L Electronic Ballast | F46ILL | 175 | 34W T-12 4' 6L Electronic Ballast | F46EL | 186 | 11
41 | 32W T-8 4' 2L VHLO Electronic Ballast | F42ILL-V | 79 | 34W T-12 4' 4L Electronic Ballast | F44EL | 120 | 41 | 2-Lamp Upgrade of a 4-Lamp Baseline
42 | 32W T-8 4' 4L RLO Electronic Ballast | F44ILL-R | 102 | 34W T-12 4' 4L Electronic Ballast | F44EL | 120 | 18
43 | 30W Super T-8 4' 1L Electronic Ballast | F41SILL | 28 | 34W T-12 4' 1L EE Magnetic Ballast | F41EL | 32 | 4 | Upgrade Fixture uses 30W Super T-8 Lamps
44 | 30W Super T-8 4' 2L Electronic Ballast | F42SILL | 53 | 34W T-12 4' 2L EE Magnetic Ballast | F42EL | 60 | 7 | Upgrade Fixture uses 30W Super T-8 Lamps
45 | 30W Super T-8 4' 3L Electronic Ballast | F43SILL | 78 | 34W T-12 4' 3L EE Magnetic Ballast | F43EL | 92 | 14 | Upgrade Fixture uses 30W Super T-8 Lamps
46 | 30W Super T-8 4' 4L Electronic Ballast | F44SILL | 105 | 34W T-12 4' 4L EE Magnetic Ballast | F44EL | 120 | 15 | Upgrade Fixture uses 30W Super T-8 Lamps
47 | 28W Super T-8 4' 1L Electronic Ballast | F41SSILL | 26 | 34W T-12 4' 1L EE Magnetic Ballast | F41EL | 32 | 6 | Upgrade Fixture uses 28W Super T-8 Lamps
48 | 28W Super T-8 4' 2L Electronic Ballast | F42SSILL | 48 | 34W T-12 4' 2L EE Magnetic Ballast | F42EL | 60 | 12 | Upgrade Fixture uses 28W Super T-8 Lamps
49 | 28W Super T-8 4' 3L Electronic Ballast | F43SSILL | 72 | 34W T-12 4' 3L EE Magnetic Ballast | F43EL | 92 | 20 | Upgrade Fixture uses 28W Super T-8 Lamps
50 | 28W Super T-8 4' 4L Electronic Ballast | F44SSILL | 96 | 34W T-12 4' 4L EE Magnetic Ballast | F44EL | 120 | 24 | Upgrade Fixture uses 28W Super T-8 Lamps
51 | 59W T-8 8' 1L Electronic Ballast | F81ILL | 58 | 60W T-12 8' 1L Electronic Ballast | F81EL | 60 | 2
52 | 59W T-8 8' 2L Electronic Ballast | F82ILL | 109 | 60W T-12 8' 2L Electronic Ballast | F82EL | 110 | 1
53 | 59W T-8 8' 4L Electronic Ballast | F84ILL | 219 | 60W T-12 8' 4L Electronic Ballast | F84EL | 220 | 1
54 | 59W T-8 8' 6L Electronic Ballast | F86ILL | 328 | 60W T-12 8' 6L Electronic Ballast | F86EL | 330 | 2
Super T-8 Linear Fluorescent Upgrade (Standard T-8 as Baseline)
55 | 28W Super T-8 4' 1L Electronic Ballast | F41SSILL | 26 | 32W T-8 4' 1L Electronic Ballast | F41ILL | 31 | 5
56 | 28W Super T-8 4' 2L Electronic Ballast | F42SSILL | 48 | 32W T-8 4' 2L Electronic Ballast | F42ILL | 59 | 11
57 | 28W Super T-8 4' 3L Electronic Ballast | F43SSILL | 72 | 32W T-8 4' 3L Electronic Ballast | F43ILL | 89 | 17
58 | 28W Super T-8 4' 4L Electronic Ballast | F44SSILL | 96 | 32W T-8 4' 4L Electronic Ballast | F44ILL | 112 | 16
T-5 HO Linear Fluorescent Upgrade (Probe Start Metal Halide as Baseline)
59 | T-5 4' 2L HO Electronic Ballast | F42GHL | 117 | Metal Halide Probe Start 150W | MH150/1 | 190 | 73 | Baseline uses constant wattage ballasts.
60 | T-5 4' 3L HO Electronic Ballast | F43GHL | 177 | Metal Halide Probe Start 175W | MH175/1 | 215 | 38 | Baseline uses constant wattage ballasts.
61 | T-5 4' 4L HO Electronic Ballast | F44GHL | 234 | Metal Halide Probe Start 250W | MH250/1 | 295 | 61 | Baseline uses constant wattage ballasts.
62 | T-5 4' 6L HO Electronic Ballast | F46GHL | 351 | Metal Halide Probe Start 400W | MH400/1 | 458 | 107 | Baseline uses constant wattage ballasts.
63 | T-5 4' 8L HO Electronic Ballast | F48GHL | 468 | Metal Halide Probe Start 1000W | MH1000/1 | 1080 | 612 | Baseline uses constant wattage ballasts.
Screw-In Compact Fluorescent (Incandescent as Baseline)
64 | Screw-In CFL 7W | CFC7/1 | 7 | Incandescent 25W | I25/1 | 25 | 18
65 | Screw-In CFL 9W | CFC9/1 | 9 | Incandescent 34W | I34/1 | 34 | 25
66 | Screw-In CFL 11W | CFC11/1 | 11 | Incandescent 40W | I40/1 | 40 | 29
67 | Screw-In CFL 13W | CFC13/1 | 13 | Incandescent 60W | I60/1 | 60 | 47
68 | Screw-In CFL 15W | CFC15/1 | 15 | Incandescent 60W | I60/1 | 60 | 45
69 | Screw-In CFL 18W | CFC18/1 | 18 | Incandescent 75W | I75/1 | 75 | 57
70 | Screw-In CFL 20W | CFC20/1 | 20 | Incandescent 75W | I75/1 | 75 | 55
71 | Screw-In CFL 23W | CFC23/1 | 23 | Incandescent 100W | I100/1 | 100 | 77
72 | Screw-In CFL 26W | CFC26/1 | 26 | Incandescent 100W | I100/1 | 100 | 74
Hard-Wire Compact Fluorescent with Magnetic Ballast (Incandescent as Baseline)
73 | Hard-Wire CFL 9W | CFT9/1 | 11 | Incandescent 34W | I34/1 | 34 | 23
74 | Hard-Wire CFL 11W | CF11/1 | 13 | Incandescent 40W | I40/1 | 40 | 27
75 | Hard-Wire CFL 13W | CFQ13/1 | 17 | Incandescent 60W | I60/1 | 60 | 43
76 | Hard-Wire CFL 15W | CFQ15/1 | 20 | Incandescent 60W | I60/1 | 60 | 40
77 | Hard-Wire CFL 17W | CFQ17/1 | 24 | Incandescent 75W | I75/1 | 75 | 51
78 | Hard-Wire CFL 18W | CFQ18/1 | 26 | Incandescent 75W | I75/1 | 75 | 49
79 | Hard-Wire CFL 20W | CFQ20/1 | 23 | Incandescent 75W | I75/1 | 75 | 52
80 | Hard-Wire CFL 22W | CFQ22/1 | 24 | Incandescent 100W | I100/1 | 100 | 76
81 | Hard-Wire CFL 23W | CF23/1 | 29 | Incandescent 100W | I100/1 | 100 | 71
82 | Hard-Wire CFL 24W | CFT24/1 | 32 | Incandescent 100W | I100/1 | 100 | 68
83 | Hard-Wire CFL 26W | CFQ26/1 | 33 | Incandescent 100W | I100/1 | 100 | 67
84 | Hard-Wire CFL 28W | CFT28/1 | 33 | Incandescent 120W | I120/1 | 120 | 87
85 | Hard-Wire CFL 36W | CFT36/1 | 51 | Incandescent 150W | I150/1 | 150 | 99
Hard-Wire Compact Fluorescent with Electronic Ballast (Incandescent as Baseline)
86 | Hard-Wire CFL 7W | CFS7/1 | 7 | Incandescent 25W | I25/1 | 25 | 18
87 | Hard-Wire CFL 9W | CFS9/1 | 9 | Incandescent 34W | I34/1 | 34 | 25
88 | Hard-Wire CFL 11W | CFS11/1 | 11 | Incandescent 40W | I40/1 | 40 | 29
89 | Hard-Wire CFL 13W | CFS13/1 | 13 | Incandescent 40W | I60/1 | 60 | 47
90 | Hard-Wire CFL 15W | CFS15/1 | 15 | Incandescent 60W | I60/1 | 60 | 45
91 | Hard-Wire CFL 20W | CFS20/1 | 20 | Incandescent 75W | I75/1 | 75 | 55
92 | Hard-Wire CFL 23W | CFS23/1 | 23 | Incandescent 100W | I100/1 | 100 | 77
93 | Hard-Wire CFL 26W | CFS26/1 | 26 | Incandescent 100W | I100/1 | 100 | 74
94 | Hard-Wire CFL 27W | CFS27/1 | 27 | Incandescent 100W | I100/1 | 100 | 73
QL Induction Upgrade (Probe Start Metal Halide as Baseline)
95 | 55W QL Induction Fixture | QL55/1 | 55 | Metal Halide Probe Start 70W | MH70/1 | 95 | 40
96 | 85W QL Induction Fixture | QL85/1 | 85 | Metal Halide Probe Start 150W | MH150/1 | 190 | 105
97 | 165W QL Induction Fixture | QL165/1 | 165 | Metal Halide Probe Start 250W | MH250/1 | 295 | 130
LED Exit Signs (Incandescent Exit Signs as Baseline)
98 | Exit Sign - LED Single Sided | ELED2/1 | 2 | Exit Sign - Incandescent Single Sided | EI20/1 | 20 | 18
99 | Exit Sign - LED Dual Sided | ELED2/2 | 4 | Exit Sign - Incandescent Dual Sided | EI20/2 | 40 | 36
Pulse Start Metal Halide Upgrade (Probe Start Metal Halide as Baseline)
100 | 150W Pulse Start Metal Halide | MHPS/SCWA/150/1 | 190 | Metal Halide Probe Start 175W | MH175/1 | 215 | 25 | Baseline is higher wattage due to higher lumen depreciation.
101 | 175W Pulse Start Metal Halide | MHPS/SCWA/175/1 | 208 | Metal Halide Probe Start 200W | MH200/1 | 232 | 24 | Baseline is higher wattage due to higher lumen depreciation.
102 | 200W Pulse Start Metal Halide | MHPS/SCWA/200/1 | 232 | Metal Halide Probe Start 250W | MH250/1 | 295 | 63 | Baseline is higher wattage due to higher lumen depreciation.
103 | 250W Pulse Start Metal Halide | MHPS/SCWA/250/1 | 288 | Metal Halide Probe Start 300W | MH300/1 | 342 | 54 | Baseline is higher wattage due to higher lumen depreciation.
104 | 300W Pulse Start Metal Halide | MHPS/SCWA/300/1 | 342 | Metal Halide Probe Start 320W | MH320/1 | 365 | 23 | Baseline is higher wattage due to higher lumen depreciation.
105 | 320W Pulse Start Metal Halide | MHPS/SCWA/320/1 | 368 | Metal Halide Probe Start 350W | MH350/1 | 400 | 32 | Baseline is higher wattage due to higher lumen depreciation.
106 | 350W Pulse Start Metal Halide | MHPS/SCWA/350/1 | 400 | Metal Halide Probe Start 400W | MH400/1 | 458 | 58 | Baseline is higher wattage due to higher lumen depreciation.
107 | 400W Pulse Start Metal Halide | MHPS/SCWA/400/1 | 450 | Metal Halide Probe Start 450W | MH450/1 | 508 | 58 | Baseline is higher wattage due to higher lumen depreciation.
108 | 750W Pulse Start Metal Halide | MHPS/SCWA/750/1 | 815 | Metal Halide Probe Start 750W | MH750/1 | 850 | 35
109 | 1000W Pulse Start Metal Halide | MHPS/SCWA/1000/1 | 1080 | Metal Halide Probe Start 1000W | MH1000/1 | 1080 | 0