Add solid samples to the internal corrosion part of the form. A completed Standard Inspection Report is to be submitted to the Director within 60 days from completion of the inspection.  A Post Inspection Memorandum (PIM) is to be completed and submitted to the Director within 30 days from the completion of the inspection, or series of inspections, and is to be filed as part of the Standard Inspection Report.

| Inspection Report | Post Inspection Memorandum |
| --- | --- |
| Inspector/Submit Date: |  | Inspector/Submit Date: |  |
|  |  | Peer Review/Date: |  |
|  |  | Director Approval/Date: |  |
| POST INSPECTION MEMORANDUM (PIM) |
| Name of Operator: |  | OPID #: |  |
| Name of Unit(s): |  | Unit #(s): |  |
| Records Location: |  | Activity # |  |
| Unit Type & Commodity: |  |
| Inspection Type: |  | Inspection Date(s): |  |
| PHMSA Representative(s): |  | AFO Days: |  |

| Company System Maps (copies for Region Files): |  |
| --- | --- |
| Validate SMART Data (components, miles, etc): |  | Acquisition(s), Sale or New Construction (submit SMART update): |  |  |
| Validate Additional Requirements Resulting From Waiver(s) or Special Permit(s): |  |

Summary:

Findings:

| Name of Operator: |  |
| --- | --- |
| OP ID No. () |  | Unit ID No. (1) |  |
| HQ Address: |  | System/Unit Name & Address: (1) |  |
| Co. Official: |  | Activity Record ID No.: |  |
| Phone No.: |  | Phone No.: |  |
| Fax No.: |  | Fax No.: |  |
| Emergency Phone No.: |  | Emergency Phone No.: |  |
| Persons Interviewed | Title | Phone No. |
| PHMSA Representative(s) (1) |  | Inspection Date(s) (1) |  |
| Company System Maps (Copies for Region Files): |  |

Counties of Operation: (list each field separately)

Storage Field(s) Description: (list each field separately)

Inspection Summary:

The attached evaluation form should be used in conjunction with 49CFR Parts 191 and 192, and PHMSA Form 1.

| PIPE TYPE |
| --- |
|  | Bare steel | Coated steel | Ineffectively Coated | Pre70-ERW | Plastic | Other: must specify type |
| Footage/Mileage |  |  |  |  |  |  |

| PIPE SPECIFICATIONS (2” AND LARGER) |
| --- |
| Diameter(s) |  |  |  |  |  |  |
| Pipe Grade(s) |  |  |  |  |  |  |
| Wall Thickness(s) |  |  |  |  |  |  |
| Footage/Mileage |  |  |  |  |  |  |

WELL STIMULATION

| ACIDIZING |
| --- |
| Acidizing treatments used to stimulate the wells? ___Yes ___No |
| Type(s) of acids used in treating the wells: |  |
| Type(s) of inhibitors used with the acid(s): |  |
| Frequency of the treatments: |  | Volume of acid per treatment: |  |
| Well cleanup procedure following treatment: |  |
| If treatment is flowed back into the well/injection line, criteria used to determine that the treatment will not cause internal corrosion or erosion of the pipe: |  |
| FRACTURING |
| Fracturing treatments used to stimulate the wells? ___ Yes ___No |
| Type(s) of fracturing fluids used in treating the wells: |  |
| Type(s) of inhibitors used with the fracturing fluid(s): |  |
| Frequency of the treatments: |  | Amount of sand per treatment: |  |
| Well cleanup procedure following treatment: |  |
| If treatment is flowed back into the well/injection line, criteria used to determine that the treatment will not cause internal corrosion or erosion of the pipe: |  |

GAS and LIQUID HANDLING FACILITIES

| GAS COMPRESSION |
| --- |
| Location of compressors: |  |
| Number, Size (HP), and Date of Installation of Units: |  |
| GAS DEHYDRATION |
| Location of dehydration units: |  |
| Type(s) of dehydration process used: |  |
| Number of dehydration units: |  | Dehydration capacity: |  |
| GAS SWEETENING (Acid Gas Treating) |
| Location of sweetening units: |  |
| Type(s) of sweetening process used: |  |
| Number of sweetening units: |  | Sweetening capacity: |  |
| GAS / LIQUID SEPARATION |
| SCRUBBERS / SEPARATORS: |  |
| Location of scrubbers/separators: |  |
| Type(s) of scrubbers/separators used: |  |
| Number of scrubbers/separators: |  | Separation capacity: |  |
| DRIPS: |  |
| Location of drips: |  |
| Type(s) of drips used: |  |
| Number of drips: |  |
| Frequency of draining or blowing drips: |  |

FIELD OPERATING PARAMETERS

| PRESSURES, RATES and TEMPERATURES |
| --- |
|  | Pressure, psi | Flow Rate, MMcf/day | Temperature, °F |
|  | Injection | Withdrawal | Injection | Withdrawal | Injection | Withdrawal |
| Minimum |  |  |  |  |  |  |
| Maximum |  |  |  |  |  |  |
| Maximum Allowable Operating Pressure (Field): |
| WATER, CO2, and O2 CONTENT |
|  | Water, lbs./MMcf | CO2, | H2S, ppm | O2, % |
| Injection Cycle |  |  |  |  |
| Withdrawal Cycle |  |  |  |  |

FIELD OPERATING AND MAINTENANCE HISTORY

| LEAKS (NON-RUPTURES) |
| --- |
| Are leak surveys of the field being conducted? (49 CFR 192.706) ___Yes ___ No |
| Have any leaks been found within last 5 years or since last DOT inspection? ___Yes ___No | Number of leaks: |
| Types of leaks that have occurred? |
| Cause(s) of the leaks: |
| Location(s) of the leaks: |
| Has a trend analysis been performed? ___ Yes ___ No |
| If a trend analysis has been done, what do the results indicate? |
| FAILURE/RUPTURES |
| Have any failures occurred within last 5 years or since last DOT inspection? ___ Yes ___ No | Number of failures: |
| Type(s) of failures that have occurred: |
| Cause(s) of the failures: |
| Location(s) of the failures: |
| Has a trend analysis been performed? ___ Yes ___ No |
| If a trend analysis has been done, what do the results indicate? |
| LINE REPLACEMENTS |
| Have any lines been replaced within last 5 years or since last DOT inspection? ___ Yes ___ No | Number of replacements: |
| Type(s) of replacements: |
| Location(s) of the replacements: |
| Reason(s) for replacements: |

| LINE REPAIRS |
| --- |
| Have any lines been repaired within last 5 years or since last DOT inspection? ___ Yes ___ No | Number of repairs: |
| Type(s) of repairs: |
| Location(s) of the repairs: |
| Reason(s) for the repairs: |
| VALVE REPLACEMENTS |
| Have any valves been replaced within last 5 years or since last DOT inspection? ___ Yes ___No | Number of replacements: |
| Type(s) of valve replacements: |
| Location(s) of the replacements: |
| Reason(s) for the replacements: |
| GAS and LIQUID HANDLING FACILITY UPSETS |
|  | Gas Dehydration Units | Gas Sweetening Units | Separators |
| Number of upsets – within last 5 years or since last DOT inspection? |  |  |  |
| Cause(s) of the upsets: |
| Has a trend analysis been performed? ___ Yes ___ No |
| If a trend analysis has been done, what do the results indicate? |

CORROSION CONTROL AND MONITORING

| EXTERNAL CORROSION |
| --- |
| Are the field piping and related storage field facilities cathodically protected? (49 CFR 192 Subpart I) ___ Yes ___No |
| Type(s) of cathodic protection used: ___ Impressed Current ___ Galvanic Anodes ___ Combination |
| Criteria used to determine adequate cathodic protection: |
| Does the field piping system contain any bare or ineffectively coated pipe? ___ Yes ___ No |
| Location(s) of the bare or ineffectively coated pipe: |
| Amount of bare of ineffectively coated pipe: |
| Are corrosion monitoring procedures established for the field piping and related storage field facilities? ___ Yes ___ No |
| MONITORING |
| Pipe-to-soil readings ___ Yes ___ No Close interval surveys ___ Yes ___ No Line current surveys ___ Yes ___ No | Exposed pipe reports ___ Yes ___ No Leak surveys ___ Yes ___ No Instrumented inspection surveys ___ Yes ___ No |
| Remedial measures taken to mitigate corrosion: |

| INTERNAL CORROSION |
| --- |
| Are corrosion monitoring procedures established for the field piping and related storage field facilities? ___ Yes ___ No |
| MONITORING |
| Corrosion coupons ___ Yes ___ No Gas samples ___ Yes ___ No Water samples ___ Yes ___ No Solids samples ___ Yes ___ No | Pipe replacement reports surveys ___ Yes ___ No Leak surveys ___ Yes ___ No Instrumental inspection surveys ___ Yes ___ No |
| CORROSION COUPONS |
| Frequency coupons are analyzed (minimum two times each calendar year, but with interval not exceeding 7 ½ months): |
| Location(s) where coupons are installed: |
| GAS SAMPLES |
| Frequency of sampling: |
| Location(s) where the samples taken: |
| Are the gas samples analyzed for: Carbon dioxide (CO2) ___ Yes ___ No Hydrogen sulfide (H2S) ___ Yes ___ No Oxygen (O2) ___ Yes ___ No Water vapor ___ Yes ___ No | Amount of the following present in the gas: |
|  | Carbon dioxide (CO2) |  |  |
|  | Hydrogen sulfide (H2S) |  |  |
|  | Oxygen (O2) |  |  |
|  | Water vapor |  |  |
| What carbon dioxide (CO2) partial pressure criteria are used to establish carbon dioxide (CO2) corrosivity ranges? |
| What is the carbon dioxide (CO2) corrosivity ranges? |
| What is the carbon dioxide (CO2) partial pressure? |
| WATER/LIQUIDS SAMPLES |
| Frequency of sampling: |
| Locations where the samples are taken: |
| What constituents are the water samples analyzed for? (Refer to the Water Analysis Checklist) |
| Concentration of the following present in water: | Amount of the following gases dissolved in the water: |
| Iron (Fe++) |  |  | Carbon dioxide (CO2) |  |  |
| Manganese (Mn++) |  |  | Hydrogen sulfide (HsS) |  |  |
| Chlorides (Cl-) |  |  | Oxygen (O2) |  |  |
| Sulfates (SO4=) |  |  |  |  |  |
| Is the pH of the water below 6.8? ___ Yes ___ No |
| Is hydrostatic test water sampled for the presence of bacteria? ___ Yes ___ No |
| Are liquids tested for evidence of excessive glycol in the pipeline, which if deteriorated, could lower the pH? ___ Yes ___ No |
| SOLIDS SAMPLES (collected at pig receivers) |
| Frequency of sampling: |
| Locations where the samples taken: |
| Are solids observed and/or tested for the following components? |
| Iron Oxide | ___ Yes ___ No | Scales | ___ Yes ___ No |
| Iron Sulfide | ___ Yes ___ No | Sand | ___ Yes ___ No |
| Is the volume of solids increasing or decreasing between pig runs? |
| Comments: |

ATMOSPHERIC CORROSION

Are corrosion monitoring procedures established for the field piping and related storage field facilities? ___ Yes ___ No

Location(s) where corrosion has been found:

Remedial measures taken to mitigate corrosion:

INSTRUMENTED INSPECTION SURVEYS

Frequency surveys are conducted:

Lines that have been surveyed and when the survey was conducted:

INHIBITOR PROGRAM

Has a corrosion inhibitor program been established for the field piping and related storage field facilities? ___ Yes ___ No

When did the program start?

Type(s) of treatment method used: ___ Batch ___ Continuous

Type(s) of inhibitors used:

Are liquid samples periodically taken to test for residual corrosion inhibitor, to help determine effectiveness? ___ Yes ___ No

MAINTENANCE PIGGING (See also solids and water sampling, inhibitor sections)

Does operator have a maintenance pigging program designed to sweep the lines of sediments and/or scale? ___ Yes ___ No

Does operator adhere to the pigging program? ___ Yes ___ No

Comments:

CONTROLLING GAS VELOCITY – INTERNAL CORROSION AND EROSION

Have target flow rates been determined for the field piping system? ___ Yes ___ No

Are injection/withdrawal flow rates kept within the targeted flow rates, to minimize sediment and water build-up, and to manage erosion? ___ Yes ___ No

Has erosion been observed during replacement of components (lines, valves, fittings, etc.)? ___ Yes ___ No

Locations where erosion has been found:

Remedial measures taken to mitigate erosion:

SAFETY DEVICES and SYSTEMS

| SURFACE FACILITIES |
| --- |
| Has a system safety analysis of the field piping and related storage facilities been performed: ___ Yes ___ No |
| Has a safety analysis function evaluation chart for the field piping and related storage field facilities been prepared? ___ Yes ___ No |
| PRESSURE SAFETY DEVICES: |
| COMPRESSORS |
| Is each compressor, per 49 CFR 192.169, equipped with pressure safety devices for overpressure protection? ___ Yes ___ No |
| Pressure protection provided by: | Location of pressure safety devices: |
| Primary |  | Primary |  |
| Secondary |  | Secondary |  |
| PRESSURE VESSELS |
| Is the working pressure of each pressure vessel (dehydrator, scrubber, etc.) equal to or greater than the MAOP? ___ Yes ___ No |
| Is each pressure vessel equipped with pressure safety devices for overpressure protection? ___ Yes ___ No |
| Pressure protection provided by: | Location of pressure safety devices: |
| Primary |  | Primary |  |
| Secondary |  | Secondary |  |
| HEADERS, LATERALS and WELL LINES |
| Are the headers, laterals and well lines equipped with pressure safety devices for overpressure protection? ___ Yes ___ No |
| Pressure protection provided by: | Location of pressure safety devices: |
| Primary |  | Primary |  |
| Secondary |  | Secondary |  |
| GAS DETECTION SAFETY DEVICES: |
| Is each compressor, per 49 CFR 192.736, building equipped with gas detection safety devices? ___ Yes ___ No |
| Are other buildings that contain gas handling equipment equipped with gas detection safety devices? ___ Yes ___ No |
| Type(s) of gas detection safety devices: ___ Combustible gas (L.E.L.) ___ Hydrogen Sulfide (H2S) ___ Other: |
| Type(s) of alarms used to notify personnel to the presence of gas: ___ Visual ___ Audible ___ Combination |
| FIRE DETECTION SAFETY DEVICES: |
| Is each compressor building equipped with fire detection safety devices? ___ Yes ___ No |
| Are other buildings that contain gas handling equipment equipped with fire detection safety devices: ___ Yes ___ No |
| Type(s) of fire detection safety devices: ___ Flame ___ Heat ___ Smoke ___ Fusible Material ___ Other: |
| Type(s) of alarms used to notify personnel to the presence of fire: ___ Visual ___ Audible ___ Combination |
| EMERGENCY SHUTDOWN SYSTEM: |
| Is each compressor station, per 49 CFR 192.167, equipped with a remote controlled emergency shutdown system? ___ Yes ___ No |
| Does the gas detection system activate the compressor station emergency shutdown system? ___ Yes ___ No |
| Does the fire detection system activate the compressor station emergency shutdown system? ___ Yes ___ No |

WELLS

Is each well equipped with a well storage safety valve? ___ Yes ___ No

If not, are there plans to equip each well with a well storage safety valve? ___ Yes ___ No

Reasons why wells should not be equipped with well storage safety valve(s)?

ADDITIONAL COMMENTS

WATER ANALYSIS CHECKLISTS

| Constituent |  | Does Operator test for: | Operator’s “threshold” | Constituent |  | Does Operator test for: | Operator’s “threshold” |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Yes | No |  |  |  | Yes | No |  |
| Sodium |  | Na+ |  |  |  |  | Chloride |  | Cl- |  |  |  |  |
| Potassium |  | K+ |  |  |  |  | Sulfate |  | SO4= |  |  |  |  |
| Calcium |  | Ca++ |  |  |  |  | Carbonate |  | CO3= |  |  |  |  |
| Magnesium |  | Mg++ |  |  |  |  | Bicarbonate |  | HCO3- |  |  |  |  |
| Iron |  | Fe++ |  |  |  |  | Hydroxide |  | OH- |  |  |  |  |
| Barium |  | Ba++ |  |  |  |  | Dissolved Oxygen |  | O2 |  |  |  |  |
| Strontium |  | Sr++ |  |  |  |  | Dissolved Carbon Dioxide |  | CO2 |  |  |  |  |
| Manganese |  | Mn++ |  |  |  |  | Dissolved Hydrogen Sulfide |  | H2S |  |  |  |  |
| Other | Does Operator test for . . . | Operator’s “threshold” | Other | Does Operator test for . . . | Operator’s “threshold” |
|  | Yes | No |  |  | Yes | No |  |
| Acidity |  |  |  | Alkalinity |  |  |  |
| pH |  |  |  | Salinity |  |  |  |
| Total Dissolved Solids (TDS) |  |  |  | Acid-producing Bacteria |  |  |  |
| Sulfate-reducing Bacteria |  |  |  |  |  |  |  |

Excessive values of the above-listed constituents and properties, dependent upon operating conditions and other factors that may be unique to the storage field, could indicate a corrosive condition in the pipeline.

| PIPELINE INSPECTION (Field) | S | U | N/A | N/C |
| --- | --- | --- | --- | --- |
| .143/(b)/.476 | Design and construction of new and replaced transmission line and components. |  |  |  |  |
| .179 | Valve Protection from Tampering or Damage |  |  |  |  |
| .463 | Cathodic Protection |  |  |  |  |
| .465 | Rectifiers |  |  |  |  |
| .479 | Pipeline Components Exposed to the Atmosphere |  |  |  |  |
| .605 | Knowledge of Operating Personnel |  |  |  |  |
| .707 | ROW Markers, Road and Railroad Crossings |  |  |  |  |
| .719 | Pre-tested Pipe (Markings and Inventory) |  |  |  |  |
| .739/.743 | Pressure Limiting and Regulating Devices (spot-check field installed equipment vs. inspection records) |  |  |  |  |
| .745 | Valve Maintenance |  |  |  |  |
| .751 | Warning Signs |  |  |  |  |
| .801 - .809 | Operator Qualification - Use PHMSA Form 15 Operator Qualification Field Inspection Protocol Form |  |  |  |  |

Comments:

| COMPRESSOR STATIONS INSPECTION (Field) (Note: Facilities may be “Grandfathered”) | S | U | N/A | N/C |
| --- | --- | --- | --- | --- |
| .143/(b)/.476 | Design and construction of new and replaced transmission line and components (excludes offshore or facilities installed or replaced before 05/23/07). |  |  |  |  |
| .163 (c) | Main operating floor must have (at least) two (2) separate and unobstructed exits |  |  |  |  |
|  | Door latch must open from inside without a key |  |  |  |  |
|  | Doors must swing outward |  |  |  |  |
| (d) | Each fence around a compressor station must have (at least) 2 gates or other facilities for emergency exit |  |  |  |  |
|  | Each gate located within 200 ft of any compressor plant building must open outward |  |  |  |  |
|  | When occupied, the door must be opened from the inside without a key |  |  |  |  |
| (e) | Does equipment and wiring in compressor stations conform to the National Electric Code, ANSI/NFPA 70? |  |  |  |  |
| .165(a) | If applicable, are there liquid separator(s) on the intake to the compressors? |  |  |  |  |
| .165(b) | Do the liquid separators have a manual means of removing liquids? |  |  |  |  |
|  | If slugs of liquid could be carried into the compressors, are there automatic dumps on the separators, Automatic compressor shutdown devices, or high liquid level alarms? |  |  |  |  |
| .167(a) | ESD system must: |  |
|  | - Discharge blowdown gas to a safe location |  |  |  |  |
|  | - Block and blowdown the gas in the station |  |  |  |  |
|  | - Shut down gas compressing equipment, gas fires, electrical facilities in compressor building and near gas headers |  |  |  |  |
|  | - Maintain necessary electrical circuits for emergency lighting and circuits needed to protect equipment from damage |  |  |  |  |
|  | ESD system must be operable from at least two locations, each of which is: |  |
|  | - Outside the gas area of the station |  |  |  |  |
|  | - Not more than 500 feet from the limits of the station |  |  |  |  |
|  | - ESD switches near emergency exits? |  |  |  |  |
| .167 (b) | For stations supplying gas directly to distribution systems, is the ESD system configured so that the LDC will not be shut down if the ESD is activated? |  |  |  |  |
| .171(a) | Does the compressor station have adequate fire protection facilities? If fire pumps are used, they must not be affected by the ESD system. |  |  |  |  |
| (b) | Do the compressor station prime movers (other than electrical movers) have over-speed shutdown? |  |  |  |  |
| (c) | Do the compressor units alarm or shutdown in the event of inadequate cooling or lubrication of the unit(s)? |  |  |  |  |
| (d) | Are the gas compressor units equipped to automatically stop fuel flow and vent the engine if the engine is stopped for any reason? |  |  |  |  |
| (e) | Are the mufflers equipped with vents to vent any trapped gas? |  |  |  |  |
| .173 | Is each compressor station building adequately ventilated? |  |  |  |  |
| .457 | Is all buried piping cathodically protected? |  |  |  |  |
| .481 | Atmospheric corrosion of aboveground facilities |  |  |  |  |
| .603 | Does the operator have procedures for the start-up and shut-down of the station and/or compressor units? |  |  |  |  |
|  | Are facility maps current/up-to-date? |  |  |  |  |
| .615 | Emergency Plan for the station on site? |  |  |  |  |
| .619 | Review pressure recording charts and/or SCADA |  |  |  |  |
| .707 | Markers |  |  |  |  |
| .731 | Overpressure protection – reliefs or shutdowns |  |  |  |  |
| .735 | Are combustible materials in quantities exceeding normal daily usage, stored a safe distance from the compressor building? |  |  |  |  |
|  | Are aboveground oil or gasoline storage tanks protected in accordance with NFPA standard No. 30? |  |  |  |  |
| .736 | Gas detection – location |  |  |  |  |

Comments:

| REPORTING PERFORMANCE AND RECORDS | S | U | N/A | N/C |
| --- | --- | --- | --- | --- |
| 191.5 | Immediate Notice of certain incidents to NRC (800) 424-8802, or electronically at http://www.nrc.uscg.mil/ , and additional report if significant new information becomes available. Operator must have a written procedure for calculating an initial estimate of the amount of product released in an accident. |  |  |  |  |
| 191.7 | Reports (except SRCR and offshore pipeline condition reports) must be submitted electronically to PHMSA at https://opsweb.phmsa.dot.gov unless an alternative reporting method is authorized IAW with paragraph (d) of this section. |  |  |  |  |
| 191.15(a) | Written incident reports; supplemental incident reports (Form 7100-2) Submittal must be electronically to http://pipelineonlinereporting.phmsa.dot.gov/ |  |  |  |  |
| 191.15(c) | Supplemental report (to 30-day follow-up) |  |  |  |  |
| 191.17(a) | Complete and submit DOT Form PHMSA F 7100-2.1 by March 15 of each calendar year for the preceding year. (NOTE: June 15, 2011 for the year 2010). |  |  |  |  |
| 191.22 | Each operator must obtain an OPID, validate its OPIDs, and notify PHMSA of certain events at https://opsweb.phmsa.dot.gov |  |  |  |  |
| 191.23 | Safety related condition reports |  |  |  |  |
| 191.25 | Filing the SRCR within 5 days of determination, but not later than 10 days after discovery |  |  |  |  |
| 192.27(g) | Abandoned facilities, onshore crossing commercially navigable waterways reports |  |  |  |  |

Comments:

| CONSTRUCTION PERFORMANCE AND RECORDS | S | U | N/A | N/C |
| --- | --- | --- | --- | --- |
| .225 | Test Results to Qualify Welding Procedures |  |  |  |  |
| .227 | Welder Qualification |  |  |  |  |
| .241(a) | Visual Weld Inspector Training/Experience |  |  |  |  |
| .243(b)(2) | Nondestructive Technician Qualification |  |  |  |  |
| (c) | NDT procedures |  |  |  |  |
| (f) | Total Number of Girth Welds |  |  |  |  |
| (f) | Number of Welds Inspected by NDT |  |  |  |  |
| (f) | Number of Welds Rejected |  |  |  |  |
| (f) | Disposition of each Weld Rejected |  |  |  |  |
| .303 | Construction Specifications |  |  |  |  |
| .325 | Underground Clearance |  |  |  |  |
| .327 | Amount, Location, Cover of each Size of Pipe Installed |  |  |  |  |
| .455 | Cathodic Protection |  |  |  |  |

| OPERATIONS and MAINTENANCE PERFORMANCE AND RECORDS | S | U | N/A | N/C |
| --- | --- | --- | --- | --- |
| .603(b) | .605(a) Procedural Manual Review – Operations and Maintenance (1 per yr/15 months) |  |  |  |  |
| .603(b) | .605(c) Abnormal Operations |  |  |  |  |
| .603(b) | .605(b)(3) Availability of construction records, maps, operating history to operating personnel |  |  |  |  |
| .603(b) | .605(b)(8) Periodic review of personnel work – effectiveness of normal O&M procedures |  |  |  |  |
| .603(b) | .605(c)(4) Periodic review of personnel work – effectiveness of abnormal operation procedures |  |  |  |  |
| .709 | .614 Damage Prevention (Miscellaneous) |  |  |  |  |
| .709 | .609 Class Location Study (If Applicable) |  |  |  |  |
| .603(b) | .615(b)(1) Location Specific Emergency Plan |  |  |  |  |
| .603(b) | .615(b)(2) Emergency Procedure training, verify effectiveness of training |  |  |  |  |
| .603(b) | .615(b)(3) Employee Emergency activity review, determine if procedures were followed. |  |  |  |  |
| .603(b) | .615(c) Liaison Program with Public Officials |  |  |  |  |
| .605(a) | .616 Public Awareness Program also in accordance with API RP 1162 |  |
|  | .616(e & f) Documentation properly and adequately reflects implementation of operator’s Public Awareness Program requirements - Stakeholder Audience identification, message type and content, delivery method and frequency, supplemental enhancements, program evaluations, etc. (i.e. contact or mailing rosters, postage receipts, return receipts, audience contact documentation, etc. for emergency responder, public officials, school superintendents, program evaluations, etc.). See table below: |  |  |  |  |
|  |  | API RP 1162 Baseline* Recommended Message Deliveries |  |  |
|  |  | Stakeholder Audience (Natural Gas Transmission Line Operators) | Baseline Message Frequency (starting from effective date of Plane) |  |  |
|  |  | Residents Along Right-of-Way and Places of Congregation | 2 years |  |  |
|  |  | Emergency Officials | Annual |  |  |
|  |  | Public Officials | 3 years |  |  |
|  |  | Excavator and Contractors | Annual |  |  |
|  |  | One-Call Centers | As required of One-Call Center |  |  |
|  |  | Stakeholder Audience (Gathering Line Operators) | Baseline Message Frequency (starting from effective date of Plan) |  |  |
|  |  | Residents and Places of Congregation | 2 years |  |  |
|  |  | Emergency Officials | Annual |  |  |
|  |  | Public Officials | 3 years |  |  |
|  |  | Excavators and Contractors | Annual |  |  |
|  |  | One-Call Centers | As required of One-Call Center |  |  |
|  | .616(g) The program must be conducted in English and any other languages commonly understood by a significant number of the population in the operator's area? |  |  |  |  |
| .517 | Pressure Testing |  |  |  |  |
| .709 | .619 Maximum Allowable Operating Pressure (MAOP) |  |  |  |  |
| .709 | .625 Odorization of Gas |  |  |  |  |
| .709 | .705 Patrolling (Refer to Table Below) |  |  |  |  |
| Class Location At Highway and Railroad Crossings At All Other Places 1 and 2 2/yr (7½ months) 1/yr (15 months) 3 4/yr (4½ months) 2/yr (7½ months) 4 4/yr (4½ months) 4/yr (4½ months) |
| .709 | .706 Leak Surveys (Refer to Table Below) |  |  |  |  |
| Class Location Required Not Exceed 1 and 2 1/yr 15 months 3 2/yr* 7½ months 4 4/yr* 4½ months * Leak detector equipment survey required for lines transporting un-odorized gas. |
| .603b/.727g | .727 Abandoned Pipelines also Underwater Facility Reports if applicable |  |  |  |  |
| .709 | .731(a) Compressor Station Relief Devices (1 per yr/15 months) |  |  |  |  |
| .709 | .731(c) Compressor Station Emergency Shutdown (1 per yr/15 months) |  |  |  |  |
| .709 | .736(c) Compressor Stations – Detection and Alarms (Performance Test) |  |  |  |  |
| .709 | .739 Pressure Limiting and Regulating Stations (1 per yr/15 months) |  |  |  |  |
| .709 | .743 Pressure Limiting and Regulator Stations – Capacity (1 per yr/15 months) |  |  |  |  |
| .709 | .745 Valve Maintenance (1 per yr/15 months) |  |  |  |  |
| .709 | .749 Vault Maintenance (>200 cubic feet)(1 per yr/15 months) |  |  |  |  |
| .603(b) | .751 Prevention of Accidental Ignition (hot work permits) |  |  |  |  |
| .603(b) | .225(b) Welding – Procedure |  |  |  |  |
| .603(b) | .227/.229 Welding – Welder Qualification |  |  |  |  |
| .603(b) | .243(b)(2) NDT – NDT Personnel Qualification |  |  |  |  |
| .709 | .243(f) NDT Records (Pipeline Life) |  |  |  |  |
| .709 | Repair: pipe (Pipeline Life); Other than pipe (5 years) |  |  |  |  |

Comments:

| CORROSION CONTROL PERFORMANCE AND RECORDS | S | U | N/A | N/C |
| --- | --- | --- | --- | --- |
| .491 | .491(a) Maps or Records |  |  |  |  |
| .491 | .459 Examination of Buried Pipe when Exposed |  |  |  |  |
| .491 | .465(a) Annual Pipe-to-soil Monitoring (1 per yr/15 months) |  |  |  |  |
| .491 | .465(b) Rectifier Monitoring (6 per yr/2½ months) |  |  |  |  |
| .491 | .465(c) Interference Bond Monitoring – Critical (6 per yr/2½ months) |  |  |  |  |
| .491 | .465(c) Interference Bond Monitoring – Non-critical (1 per yr/15 months) |  |  |  |  |
| .491 | .465(d) Prompt Remedial Actions |  |  |  |  |
| .491 | .465(e) Unprotected Pipeline Surveys, CP active corrosion areas (1 per 3 cal yr/39 months) |  |  |  |  |
| .491 | .467 Electrical Isolation (Including Casings) |  |  |  |  |
| .491 | .469 Test Stations – Sufficient Number |  |  |  |  |
| .491 | .471 Test Lead Maintenance |  |  |  |  |
| .491 | .473 Interference Currents |  |  |  |  |
| .491 | .475(a) Internal Corrosion; Corrosive Gas Investigation |  |  |  |  |
| .491 | .475(b) Internal Corrosion; Internal Surface Inspection; Pipe Replacement |  |  |  |  |
| .476(d) | .476 Internal Corrosion Control: Design and construction of transmission line |  |  |  |  |
| .491 | .477 Internal Corrosion Control Coupon Monitoring (2 per yr/7½ months) |  |  |  |  |
| .491 | .481 Atmospheric Corrosion Control Monitoring (1 per 3 cal yr/39 months onshore; 1 per yr/15 months offshore) |  |  |  |  |
| .491 | .483/.485 Remedial: Replaced or Repaired Pipe; coated and protected; corrosion evaluation and actions |  |  |  |  |

Comments:

| PART 199 – DRUG and ALCOHOL TESTING REGULATIONS and PROCEDURES | S | U | N/A | N/C |
| --- | --- | --- | --- | --- |
| Subparts A - C | Drug & Alcohol Testing & Alcohol Misuse Prevention Program – Use PHMSA Form # 13, PHMSA Drug and Alcohol Questions |  |

# Footnotes

Information not required if included on page 1.