## Manual
Pennsylvania Act 129 Motor & VFD Audit and Design Tool
MANUAL
Table of Contents:
I. Purpose
II. Organization
III. User Guide
IV. Disclaimer
I. Purpose
The purpose of the Motor & VFD Audit and Design Tool is two-fold:
1. To document the pre- and post-installation cases.
2. To facilitate the calculation of energy savings and demand reduction for motor and VFD installations.
II. Organization
The Motor & VFD Audit and Design Tool is organized into 6 sheets.
(1) Manual
The "Manual" sheet contains the instruction manual for using the Motor & VFD Audit and Design Tool.
(2) Changelog
The "Changelog" sheet provides a brief description of major changes from the previous version.
(3) Motor Form
The "Motor Form" sheet collects all relevant information to calculate energy savings and peak demand reduction for Motors. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross energy savings for evaluation purposes. Note that the requirements of Section 3.3 (Premium Efficiency Motors) in the 2013 TRM restricts the protocol to only motor replacements without VFDs. This form must be used to calculate savings for motor replacement measures only (i.e. replacement of old motors with new energy efficient motors of the same rated horsepower).
The baseline motor and configuration details should be entered in the "Pre-Installation Data" section (rows 8-25) with no VFD, and the energy efficient motor and configuration details should be entered in the "Post-Installation Data" section (rows 26-42) with no VFD. The energy and peak demand savings resulting from the motor replacement alone will be automatically calculated in cells D45 and D46 respectively. To find out how to calculate savings resulting from VFD measures, refer to the notes described below.
If the project scope includes more than 10 motors, click on the macro button next to the general information section in order to increase the number of line motor items for your convenience.
(4) Motor Custom Input
The "Motor Custom Input" sheet contains a table that allows additional customization of the "Motor Form" for motors with non-standard horsepowers. This sheet is required when a custom selection is made in column L of the "Motor Form" tab.
(5) VFD Form
The "VFD Form" sheet collects all relevant information to calculate energy savings and peak demand reduction for VFDs. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross energy savings for evaluation purposes. This form must be used to calculate savings for VFD measures only, not the combination of new motors and VSDs.
The motor and configuration details should be entered in the "VFD Installation Data" section (rows 10-24) for a motor with VFD. Select the baseline configuration details from the pull down menu. The ESF and DSF values are automatically populated in columns N and O. The energy and peak demand savings resulting from installation of VFD alone will be automatically calculated in cells D28 and D29 respectively. Note that custom protocols must be followed if the existing motor already has a VFD installed or if the VFD Baseline is not listed in the options.
If the project scope includes more than 10 motors, click on the macro button next to the general information section in order to increase the number of line motor items for your convenience.
(6) Summary
The "Summary" sheet summarizes the energy and peak demand savings for the entire project based on the calculations in "Motor Form" and "VFD Form" sheets.
a) Use the "Motor Form" to calculate savings resulting from Motor replacements only.
b) Use the "VFD Form" to calculate savings resulting from VFD installation only either on existing motor or energy efficient motor.
c) Add savings from the "Motor Form" and "VFD Form" sheets for projects with combination of both (VFDs and motor replacement).
(7) Glossary
The "Glossary" sheet is a reference for the "Motor and VFD Form" sheet. It defines each of the columns for clarification.
III. User Guide
The tool contains all information regarding motors and VFDs required for the calculation of savings pursuant to the PA TRM. The use of this tool is encouraged but not required. Users of the Motor and VFD Audit and Design Tool must complete the "Motor Form" and "VFD Form" depending on the measures installed for the project. For VFD measures in conjunction with a motor replacement measure, the savings must be calcualted separately using the "Motor Form" and "VFD Form". To find out how to calculate savings resulting from motor replacement and VFD measures separately, refer to the notes described above. The designer must select the appropriate facility type, utility, and program year from the drop down menu. Use one line on the pre-installation table and post-installation table for each unique motor, i.e. motors with different operating conditions or different motor specifications. Complete all yellow fields to calculate the peak demand reduction and annual energy savings. Pink fields are computed automatically. Roll mouse over the field heading for additional help. Projects within facility types or motor functions not included on the drop down menu must follow custom protocols to determine appropriate run hours and ESF/DSF values. Motor replacements with the following conditions should also follow custom protocols:
* Variable frequency drive (VFD) control on the existing (baseline) motor
* Two-speed motor (existing and/or new)
* Single speed motor with variable loading (not standard)
* Abnormal motor loading (i.e., load factor differs from 0.75)
* Industrial process applications
* Applications where the building type or motor usage group is not listed in Table 3-17 of the 2014 TRM
* New motor has a different rated horsepower than the existing motor
* Change in annual operating hours is anticipated
IV. Disclaimer
This document does not modify any requirements of the PA TRM and is provided for convenience only. If any discrepancy between the TRM and this document exist, the TRM should be followed.

## Changelog
Pennsylvania Act 129 Lighting Audit and Design Tool
CHANGELOG
Version 7 (Effective June 3, 2010)
1) | Released with TRM Order in June 2010
Version 8 (Submitted October 27, 2011. Effective June 1, 2011)
1) | Created Changelog
2) | Revised "Manual" and "Glossary" to improve user guide and increase usability
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM
Version 9 (Submitted September 13, 2011 for 2012 TRM Tentative Order)
1) | In "Motor and VFD Form", revised formulas in Columns O, P, and S to correct referencing errors
2) | In "Motor and VFD Form", added Column Q (Full Load kW) to correct a calculation error incorrectly applying DSF
3) | In "Motor and VFD Form", revised Column G (Coincidence Factor) to reflect TRM values (0.74 for single, 0.37 for duplex)
4) | In "Glossary", revised definition of coincidence factor to reflect above change.
5) | In "Glossary", added definition for "Full Load kW"
6) | In "Glossary", revised definition of "Nominal Efficiency" to reflect ability to custom input efficiency values for the new motor efficiency and baseline motor efficiency if the new motor is for new construction or replace on burnout.
7) | In "Manual", updated TRM reference from Table 6-12 to Table 3-15
Version 10 (Submitted December 5, 2011 for 2012 TRM Final Order)
1) | In "Motor and VFD Form", updated operating hours lookup table to reflect TRM table.
2) | In "Motor and VFD Form", corrected formulas for efficiency lookups, post-installation peak kW calculation, and total kWh calculation for post-installation line item #7.
3) | In "Motor and VFD Form", updated form to include new ESF and DSF values.
4) | In "Glossary", updated entries to reflect new column O and definition of "baseline".
Version 11 (Submitted August 31, 2012 for 2013 TRM Tentative Order)
1) | Created "Motor Form" and "VFD Form" to calculate savings for motors and VFD measures separately to be consistent with TRM protocols.
2) | In "Motor Form" and "VFD Form", updated operating hours lookup table to reflect TRM table.
3) | In "VFD Form", updated ESF and DSF values lookup table to reflect TRM table.
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D
Version 12 (Submitted December 07, 2012 for 2013 TRM Final Order)
1) | Changed the definition of "Load Factor" in Glossary to be consistent with TRM protocols.
Version 13 (Submitted August 29, 2013 for 2014 TRM Tentative Order)
1) | Revised the algorithms in Column R of the "VFD Form" tab used to calculate energy and peak demand savings to be consistent with TRM protocols. Removed a conversion factor of 0.746 to convert from HP to kW.
Version 13 (Submitted December 05, 2013 for 2014 TRM Final Order)
1) | Updated motor efficiency tables to reflect new changes to the TRM.
2) | Removed motor efficiency tables from "VFD Form".
3) | Revised "Motor Form" and added "Motor Custom Input" to allow for addition of custom motor applications.
4) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D.
Version 14 (Submitted August 05, 2014)
1) | Updated motor efficiency tables to reflect new changes to the TRM.
2) | Updated "Coincidence Factor" , "Operating Hours" and "Facility Type" lookup tables to reflect new changes to the TRM.
3) | Formulas for Coincidence Factor and Operating hours are updated to reflect changes to the TRM.
4) | Consolidated all lookup tables under single tab "Lookup Tables"; updated references to lookup tables.
5) | Added "City" to the general information section for "Motor Form" , "VFD Form" , "Motor Custom Input" and "Summary"
6) | Linked general information cells of "Motor Form" , "VFD Form" and "Motor Custom Input" to cells in "Summary". Locked the cells to protect their links.
7) | Motor Configuration column is deleted from "Motor Form" and "VFD Form"
8) | Installation date cell is modified to allow entry of a date between 6/1/2015 and 5/31/2016 only. For all other dates , an error message is displayed.
9) | Program Year is limited to Program Year 7.
10) | "VFD on Motor" column is deleted from "VFD Form". The formulas for ESF, DSF and Full Load kW are updated to exclude the deleted column.
11) | "Full Load kW" on "VFD Form" revised - previously displayed a horsepower value. "Peak kW" and "Annual kWh" adjusted to account for change made to "Full Load kW."
12) | Introduced a macro button on "Motor Form" and "VFD Form" that increases number of motor line items for user's convenience.
13) | Added 900 RPM option to "Synchronous Speed" for "Motor Form", "VFD Form" and "Motor Custom Form."
14) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D.
15) | References to "Hot Water Pump" changed to "Heating Hot Water Pump" to be consistent with TRM. References to "HWP" changed to "HHWP."

## Motor Form
Motor Inventory Form (Data Entry in Summary Tab) | [6 empty] | Appendix D of the PA TRM |  | Complete one copy of this form for each building with a motor measure
Applicant Name: |  | 0 |  |  |  |  | Project Name: |  |  | 0
Facility Name: |  | 0 |  |  |  |  | Survey completed by (name): |  |  | 0
Facility Type: |  | 0 |  |  |  |  | Spot Measurements completed by (name): |  |  | 0
Utility: |  | 0 |  |  |  |  | Date(s) Survey completed: |  |  | 0
Installation Date: |  | 0 |  |  |  |  | Program Year: |  |  | Program Year 7
[7 empty] | City: |  |  | 0
Pre-Installation Data (Equipment Survey of Existing Motors)
[8 empty] | Nameplate Data | [5 empty] | Pre-Installation Energy Consumption
Line Item | Unique Motor I.D.(s) | Motor Function | Number of Identical Units | Load Factor (LF) | Configuration Details | Motor Subtype | Coincidence Factor (CF) | Manufacturer | Model Number | Motor Horsepower | Synchronous Speed (RPM) | Enclosure Type | Nominal Efficiency | Total per Unit |  |  |  | Total all Units
[14 empty] | Full Load kW | Peak kW | Operating Hours | Annual kWh | Peak kW | Annual kWh
ex. | CHWP-1 | CHWP | 2 | 0.75 | Other | Subtype I | 0.45745 | Acme | 10000 | 50 | 1800 | ODP | 94.5% | 29.6032 | 22.3 | 3306.6364 | 48430 | 44.5 | 96860
1 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [5 empty] | 0% |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
2 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [5 empty] | 0% |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
3 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [5 empty] | 0% |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
4 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [5 empty] | 0% |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
5 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [5 empty] | 0% |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
6 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [5 empty] | 0% |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
7 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [5 empty] | 0% |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
8 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [5 empty] | 0% |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
9 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [5 empty] | 0% |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
10 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [5 empty] | 0% |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
[18 empty] | 0 | 0
Post-Installation Data (Equipment Survey of Proposed Motors)
[8 empty] | Nameplate Data | [5 empty] | Post-Installation Energy Consumption
Line Item | Unique Motor I.D.(s) | Motor Function | Number of Identical Units | Load Factor (LF) | Configuration Details | Motor Subtype | Coincidence Factor (CF) | Manufacturer | Model Number | Motor Horsepower | Synchronous Speed (RPM) | Enclosure Type | Nominal Efficiency | Total per Unit |  |  |  | Total all Units
[14 empty] | Full Load kW | Peak kW | Operating Hours | Annual kWh | Peak kW | Annual kWh
ex. | CHWP-1 | CHWP | 2 | 0.75 | Other | Subtype I | 0.45745 | Acme | 20000 | 50 | 1800 | ODP | 95.5% | 29.2932 | 13.4003 | 3306.6364 | 96861.9396 | 26.8005 | 193723.8791
1 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [8 empty] | Not Available for Selected Facility Type and Motor Function | BLANK
2 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [8 empty] | Not Available for Selected Facility Type and Motor Function | BLANK
3 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [8 empty] | Not Available for Selected Facility Type and Motor Function | BLANK
4 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [8 empty] | Not Available for Selected Facility Type and Motor Function | BLANK
5 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [8 empty] | Not Available for Selected Facility Type and Motor Function | BLANK
6 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [8 empty] | Not Available for Selected Facility Type and Motor Function | BLANK
7 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [8 empty] | Not Available for Selected Facility Type and Motor Function | BLANK
8 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [8 empty] | Not Available for Selected Facility Type and Motor Function | BLANK
9 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [8 empty] | Not Available for Selected Facility Type and Motor Function | BLANK
10 | [6 empty] | Not Available for Selected Facility Type and Motor Function | [8 empty] | Not Available for Selected Facility Type and Motor Function | BLANK
[18 empty] | 0 | 0
Savings Data
Total Peak kW Reduction |  |  | 0
Total Annual kWh Savings |  |  | 0
CLICK HERE to Increase Number of Motor Line Items
Note on B10: Unique Motor I.D. Provide designation to identify the motor(s).
Note on C10: Motor Function Select a motor function from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine Run Hours for motor functions not listed. FM: Fan Motor CHWP/CTF: Chilled Water Pump/ Cooling Tower Fan HWP: Heating Hot Water Pump
Note on D10: Number of Identical Units Number of motors that have the same motor function, load factor, configuration, manufacturer, model number, horsepower, speed, enclosure type, efficiency, and presence of VFD.
Note on E10: Load Factor Default Load Factor is 0.75. Customers wishing to adjust load factor must follow Custom Protocols for Motors and VFDs.
Note on F10: Configuration Details: This describes a specialty setup in which the motor operates. For example, a motor may be a U-frame, design C motor, close-coupled pump motor, footless motor, etc. The motor subtype and efficiency are dependent on the additional configuration details.
Note on I10: Manufacturer Provide the motor manufacturer's name.
Note on J10: Model Number Provide the motor model number.
Note on K10: Motor Horsepower Select the rated horsepower of the motor.
Note on L10: Synchronous Speed Select one of the following: 1200 RPM = 6-pole 1800 RPM = 4-pole 3600 RPM = 2-pole
Note on M10: Enclosure Type Select the motor enclosure type: TEFC: Totally Enclosed Fan Cooled ODP: Open Drip Proof
Note on N10: Nominal Efficiency Select Motor Horsepower, Synchronous Speed and Enclosure Type to determine nominal efficiency.
Note on H15: Suleyman Kemal Betin: The formula changed to lookup CF in Table 3-17A
Note on Q15: Suleyman Kemal Betin: The formula changed to lookup Operating Hours in Table 3-17
Note on B28: Unique Motor I.D. Provide designation to identify the motor(s).
Note on C28: Motor Function Select a motor function from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine Run Hours for motor functions not listed. FM: Fan Motor CHWP/CTF: Chilled Water Pump/ Cooling Tower Fan HWP: Heating Hot Water Pump
Note on D28: Number of Identical Units Number of motors that have the same motor function, load factor, configuration, manufacturer, model number, horsepower, speed, enclosure type, efficiency, and presence of VFD.
Note on E28: Load Factor Default Load Factor is 0.75. Customers wishing to adjust load factor must follow Custom Protocols for Motors and VFDs.
Note on F28: Configuration Details: This describes a specialty setup in which the motor operates. For example, a motor may be a U-frame, design C motor, close-coupled pump motor, footless motor, etc. The motor subtype and efficiency are dependent on the additional configuration details.
Note on I28: Manufacturer Provide the motor manufacturer's name.
Note on J28: Model Number Provide the motor model number.
Note on K28: Motor Horsepower Input the rated horsepower of the motor.
Note on L28: Synchronous Speed Select one of the following: 1200 RPM = 6-pole 1800 RPM = 4-pole 3600 RPM = 2-pole
Note on M28: Enclosure Type Select the motor enclosure type: TEFC: Totally Enclosed Fan Cooled ODP: Open Drip Proof
Note on N28: Nominal Efficiency Input nominal efficiency from the motor nameplate
Note on H33: Suleyman Kemal Betin: The formula changed to lookup CF in Table 3-17A
Note on Q33: Suleyman Kemal Betin: The formula changed to lookup Operating Hours in Table 3-17

## VFD Form
VFD Inventory Form (Data Entry in Summary Tab) | [6 empty] | Appendix D of the PA TRM |  | Complete one copy of this form for each building with a VFD measure
Applicant Name: |  | 0 |  |  |  |  | Project Name: |  |  | 0
Facility Name: |  | 0 |  |  |  |  | Survey completed by (name): |  |  | 0
Facility Type: |  | 0 |  |  |  |  | Spot Measurements completed by (name): |  |  | 0
Utility: |  | 0 |  |  |  |  | Date(s) Survey completed: |  |  | 0
Installation Date: |  | 0 |  |  |  |  | Program Year: |  |  | Program Year 7
[7 empty] | City: |  |  | 0
VFD Installation Data (Equipment Survey of Existing or Proposed Motors)
[6 empty] | Nameplate Data | [5 empty] | Post-Installation Energy Consumption
Line Item | Unique Motor I.D.(s) | Motor Function | Number of Identical Units | Load Factor (LF) | Coincidence Factor (CF) | Manufacturer | Model Number | Motor Horsepower | Synchronous Speed (RPM) | Enclosure Type | Nominal Efficiency | VFD |  |  |  | Total Savings per Unit |  |  | Total Savings all Units
[12 empty] | Baseline | ESF | DSF | Full Load kW | Peak kW | Operating Hours | Annual kWh | Peak kW | Annual kWh
ex. | CHWP-1 | CHWP | 2 | 0.75 | 0.45745 | Acme | 10000 | 50 | 1800 | ODP | 93% | AFBI | 0.354 | 0.26 | 40.3 | 7.8 | 3306.6364 | 22981 | 15.5 | 45963
1 |  |  |  |  | Not Available for Selected Facility Type and Motor Function | [7 empty] | BLANK | BLANK |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
2 |  |  |  |  | Not Available for Selected Facility Type and Motor Function | [7 empty] | BLANK | BLANK |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
3 |  |  |  |  | Not Available for Selected Facility Type and Motor Function | [7 empty] | BLANK | BLANK |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
4 |  |  |  |  | Not Available for Selected Facility Type and Motor Function | [7 empty] | BLANK | BLANK |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
5 |  |  |  |  | Not Available for Selected Facility Type and Motor Function | [7 empty] | BLANK | BLANK |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
6 |  |  |  |  | Not Available for Selected Facility Type and Motor Function | [7 empty] | BLANK | BLANK |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
7 |  |  |  |  | Not Available for Selected Facility Type and Motor Function | [7 empty] | BLANK | BLANK |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
8 |  |  |  |  | Not Available for Selected Facility Type and Motor Function | [7 empty] | BLANK | BLANK |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
9 |  |  |  |  | Not Available for Selected Facility Type and Motor Function | [7 empty] | BLANK | BLANK |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
10 |  |  |  |  | Not Available for Selected Facility Type and Motor Function | [7 empty] | BLANK | BLANK |  |  | Not Available for Selected Facility Type and Motor Function | BLANK
Savings Data
Total Peak kW Reduction
Total Annual kWh Savings
CLICK HERE to Increase Number of Motor Line Items
Note on B10: Unique Motor I.D. Provide designation to identify the motor(s).
Note on C10: Motor Function Select a motor function from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine Run Hours for motor functions not listed. FM: Fan Motor CHWP/CTF: Chilled Water Pump/ Cooling Tower Fan HWP: Heating Hot Water Pump
Note on D10: Number of Identical Units Number of motors that have the same motor function, load factor, configuration, manufacturer, model number, horsepower, speed, enclosure type, efficiency, and presence of VFD.
Note on E10: Load Factor Default Load Factor is 0.75. Customers wishing to adjust load factor must follow Custom Protocols for Motors and VFDs.
Note on G10: Manufacturer Provide the motor manufacturer's name.
Note on H10: Model Number Provide the motor model number.
Note on I10: Motor Horsepower Input the rated horsepower of the motor.
Note on J10: Synchronous Speed Select one of the following: 1200 RPM = 6-pole 1800 RPM = 4-pole 3600 RPM = 2-pole
Note on K10: Enclosure Type Select the motor enclosure type: TEFC: Totally Enclosed Fan Cooled ODP: Open Drip Proof
Note on L10: Nominal Efficiency Input nominal efficiency from the motor nameplate. a) Input nameplate efficiency from exisiting motor if a VFD is installed on existing motor. b) Input nameplate efficiency from efficient motor if VFD is installed with motor replacement.
Note on M11: VFD Baseline Select a VFD Baseline from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine ESF and DSF for VFD Baseline not listed. AFBI: Air Foil/Backward Incline AFBI IGV: Air Foil/Backward Incline with Inlet Guide Vanes FC: Forward Curved FC IGV: Forward Cureved with Inlet Guide Vanes CV: Constant Volume CHWP: Chilled Water Pump HWP: Heating Hot Water Pump
Note on N11: ESF "Energy Savings Factor" for the VFD. Percentage of energy consumption by motor when VFD is installed.
Note on O11: DSF "Demand Savings Factor" for the VFD. Percentage of peak demand consumption by motor when VFD is installed.
Note on T25: Gwaltney, Doug: Update formula. Suleyman Kemal Betin The formula is updated so that it will return blank if V15 is blank.
Note on U25: Gwaltney, Doug: Update formula. Suleyman Kemal Betin The formula is updated so that it will return blank if W15 is blank.

## Motor Custom Input
Applicant Name: |  | 0 |  |  |  | Project Name: | 0
Facility Name: |  | 0 |  |  |  | Survey completed by (name): | 0
Facility Type: |  | 0 |  |  |  | Spot Measurements completed by (name): | 0
Utility: |  | 0 |  |  |  | Date(s) Survey completed: | 0
Installation Date: |  | 0 |  |  |  | Program Year: | Program Year 7
[6 empty] | City: | 0
Table 1 - Defining Efficiencies for motors with "Custom" Horsepower
| Entry | Motor Horsepower | Synchronous Speed (RPM) | Enclosure Type | Nominal Efficiency
| Custom 1 | Edit | Edit | Edit | Edit
| Custom 2 | Edit | Edit | Edit | Edit
| Custom 3 | Edit | Edit | Edit | Edit
Note:
1. Complete tables only as required by the User's Guide.

## Summary
Savings Summary Form
Applicant Name: |  | Project Name:
Facility Name: |  | Survey completed by (name):
Facility Type: |  | Spot Measurements completed by (name):
Utility: |  | Date(s) Survey completed:
Installation Date: |  | Program Year: | Program Year 7
City:
Savings Data
Total Peak kW Reduction | BLANK
Total Annual kWh Savings | BLANK
Note on C4: Facility Type Select the appropriate facility type from the pull down menu.
Note on C5: Utility Select the utility serving the facility from the pull down menu.
Note on K6: Program Year: Program Year 7: June 1, 2015 - May 31, 2016
Note on K7: Suleyman Kemal Betin: Added input cell for City

## Glossary
Pennsylvania Act 129 Motor and VFD Audit and Design Tool
GLOSSARY
Motor Form |  | VFD Form
Project Identification |  | Project Identification
Cell C2: | "Applicant Name" is the applicant name. | Cell C2: | "Applicant Name" is the applicant name.
Cell C3: | "Facility Name" is the facility name. | Cell C3: | "Facility Name" is the facility name.
Cell C4: | "Facility Type" is the facility classification. The categories are based on the PA TRM. "Other" should be used when no other category is sufficient. | Cell C4: | "Facility Type" is the facility classification. The categories are based on the PA TRM. "Other" should be used when no other category is sufficient.
Cell C5: | "Utility" is the electric distribution company territory where the facility is located. | Cell C5: | "Utility" is the electric distribution company territory where the facility is located.
Cell C6: | "Date Submitted" is the date at which the application was submitted to the program. | Cell C6: | "Date Submitted" is the date at which the application was submitted to the program.
Cell K2: | "Project Name" is the name of the project. | Cell K2: | "Project Name" is the name of the project.
Cell K3: | "Survey Completed by (Name)" is the name of the inspector(s) who completed the survey. | Cell K3: | "Survey Completed by (Name)" is the name of the inspector(s) who completed the survey.
Cell K4: | "Spot Measurements Completed by (Name)" is the name of the inspector(s) who completed the spot measurements. | Cell K4: | "Spot Measurements Completed by (Name)" is the name of the inspector(s) who completed the spot measurements.
Cell K5: | "Date Survey(s) Completed" is the date at which the surveys were completed. | Cell K5: | "Date Survey(s) Completed" is the date at which the surveys were completed.
Cell K6: | "Program Year" is the program year in which the project was approved. | Cell K6: | "Program Year" is the program year in which the project was approved.
Cell K7: | "City" is the closest reference city. | Cell K7: | "City" is the closest reference city.
Motor Data |  | Motor Data
Column A: | "Line Item" indexes the motors. | Column A: | "Line Item" indexes the motors.
Column B: | "Unique Motor I.D.(s)" is an identifier for each motor. | Column B: | "Unique Motor I.D.(s)" is an identifier for each motor.
Column C: | "Motor Function" defines the function of the motor or the process served by the motor. There are three pre-defined motor functions: Fan Motor (FM), Chilled Water Pump (CHWP)/Cooling Tower Fan (CTF), and Heating Hot Water Pump (HWP). All other motor functions must be submitted as a custom measure. The combination of motor function, building type, and utility service territory determines the operating hours (column P). | Column C: | "Motor Function" defines the function of the motor or the process served by the motor. There are three pre-defined motor functions: Fan Motor (FM), Chilled Water Pump (CHWP)/Cooling Tower Fan (CTF), and Heating Hot Water Pump (HWP). All other motor functions must be submitted as a custom measure. The combination of motor function, building type, and utility service territory determines the ESF, DSF, and operating hours (columns P, Q and T).
Column D: | "Number of Identical Units" defines the quantity of motors for this particular line item. Motors that are not identical in Manufacturer, Model Number, Motor Function, Motor Configuration, Load Factor, Run Hours, Horsepower, Synchronous Speed, Enclosure Type, or Efficiency must be entered on separate lines. | Column D: | "Number of Identical Units" defines the quantity of motors for this particular line item. Motors that are not identical in Manufacturer, Model Number, Motor Function, Motor Configuration, Load Factor, Run Hours, Horsepower, Synchronous Speed, Enclosure Type, or Efficiency must be entered on separate lines.
Column E: | "Load Factor" is the ratio between the actual load and the rated load. Motor efficiency curves typically result in motors being most efficient at approximately 75% of the rated load. The default value is 0.75. | Column E: | "Load Factor" is the ratio between the actual load and the rated load. Motor efficiency curves typically result in motors being most efficient at approximately 75% of the rated load. The default value is 0.75.
Column F: | "Configuration Details" describes a specialty setup in which the motor operates. For example, a motor may be a U-frame, design C motor, close-coupled pump motor, footless motor, etc. The motor subtype and efficiency are dependent on the additional configuration details. | Column F: | "Coincidence Factor" is the percentage of the motor load that is operating during electric system’s summer peak period as defined by Act 129. This percentage is stipulated by building type and motor function.
Column G: | "Motor Subtype" is the NEMA Category under which the motor falls, and will be used to determine the standard efficiency of the motor configuration.
Column H: | "Coincidence Factor" is the percentage of the motor load that is operating during electric system’s summer peak period as defined by Act 129. This percentage is stipulated by building type and motor function.
Nameplate Data
|  | Column G: | "Manufacturer" is the maker of the motor.
|  | Column H: | "Model Number" is the specific model number of the motor.
|  | Column I: | "Motor Horsepower" is the rated horsepower of the motor.
|  | Column J: | "Synchronous Speed" is the speed at which an induction motor will operate, which depends on the input power frequency and the number of electrical magnetic poles in the motor. Select either 900 RPM, 1200 RPM, 1800 RPM, or 3600 RPM from the drop down menu.
Nameplate Data
Column I: | "Manufacturer" is the maker of the motor. | Column K: | "Enclosure Type" is the enclosure of the fan which enables the cooling of motor windings. Select "ODP" for Open Drip Proof enclosure or "TEFC" for Totally Enclosed Fan Cooled from the drop down menu.
Column J: | "Model Number" is the specific model number of the motor.
Column K: | "Motor Horsepower" is the rated horsepower of the motor.
Column L: | "Synchronous Speed" is the speed at which an induction motor will operate, which depends on the input power frequency and the number of electrical magnetic poles in the motor. Select either 900 RPM, 1200 RPM, 1800 RPM, or 3600 RPM from the drop down menu. | Column L: | "Nominal Efficiency" is the ratio of the motor shaft output power to the electric input power. If the new motor is for new construction or to replace a failed motor, the baseline motor efficiency is the code standard. Complete Columns J, K, and L to populate the efficiency automatically. If the new motor is replacing a functioning motor, input the efficiency of the existing motor. For the new motor, directly input the nameplate efficiency.
Column M: | "Enclosure Type" is the enclosure of the fan which enables the cooling of motor windings. Select "ODP" for Open Drip Proof enclosure or "TEFC" for Totally Enclosed Fan Cooled from the drop down menu.
Column N: | "Nominal Efficiency" is the ratio of the motor shaft output power to the electric input power. If the new motor is for new construction or to replace a failed motor, the baseline motor efficiency is the code standard. Complete Columns J, K, and L to populate the efficiency automatically. If the new motor is replacing a functioning motor, input the efficiency of the existing motor. For the new motor, directly input the nameplate efficiency. | VFD
|  | Column M: | "Baseline" is the baseline for the VFD system, i.e. the control system previously in place before installing the new VFD system.
|  | Column N: | "ESF" is the Energy Savings Factor for VFDs or the ratio of the motor energy usage with a VFD installed to the motor energy usage without a VFD installed. Motors with no VFD installed have an ESF of "1.00". This value can be looked up based on the baseline system.
Total per Unit
Column O: | "Full Load kW" is the maximum demand for the motor. This does not necessarily correspond to the peak demand, as coincidence factor has not been applied. | Column O: | "DSF" is the Demand Savings Factor for VFDs or the ratio of the motor peak demand with a VFD installed to the motor peak demand without a VFD installed. Motors with no VFD installed have a DSF of "1.00". This value can be looked up based on the baseline system.
Column P: | "Peak kW" is the peak demand consumption for one motor in kilowatts.
Column Q: | "Operating Hours" is the number of hours that the motor runs in one year. This number is stipulated by building type and motor function.
Column R: | "Annual kWh" is the total annual energy consumption of one motor in kilowatt-hours. | Total per Unit
|  | Column P: | "Full Load kW" is the maximum demand for the motor. This does not necessarily correspond to the peak demand, as coincidence factor has not been applied.
Total all Units
Column S: | "Peak kW" is the peak demand consumption of all the motors. | Column Q: | "Peak kW" is the peak demand consumption for one motor in kilowatts.
Column T: | "Annual kWh" is the total annual energy consumption of all the motors. | Column R: | "Operating Hours" is the number of hours that the motor runs in one year. This number is stipulated by building type and motor function.
|  | Column S: | "Annual kWh" is the total annual energy consumption of one motor in kilowatt-hours.
Total all Units
|  | Column T: | "Peak kW" is the peak demand consumption of all the motors.
|  | Column U: | "Annual kWh" is the total annual energy consumption of all the motors.

## Lookup Tables
| Baseline Motor Efficiencies, Subtype I | [6 empty] | Baseline Motor Efficiencies, Subtype II
[18 empty] | Table 3-17 (Annual Run Hours) |  | CHWP | CTF | CW Pump | HHWP | SF |  | Table 3-17A (CF) |  | CHWP | CTF | CW Pump | HHWP | SF
Motor Functions | HP | ODP1200 | ODP1800 | ODP3600 | TEFC1200 | TEFC1800 | TEFC3600 | HP | ODP900 | ODP1200 | ODP1800 | ODP3600 | TEFC900 | TEFC1200 | TEFC1800 | TEFC3600 | Allentown | Assembly | Allentown Assembly | #N/A | #N/A | #N/A | #N/A | 5187.8264 | Allentown | Assembly | Allentown Assembly | #N/A | #N/A | #N/A | #N/A | 0.52664
CHWP | 1 | 82.5% | 85.5% | 77% | 82.5% | 85.5% | 77% | 1 | 74% | 80% | 82.5% | N/A | 74% | 80% | 82.5% | 75.5% | Allentown | Education - Community College | Allentown Education - Community College | 2868.1579 | 2867.8571 | 2611.4286 | 4453.8571 | 5972.4949 | Allentown | Education - Community College | Allentown Education - Community College | 0.42302 | 0.4231 | 0.4231 | 0.010634 | 0.43972
CTF | 1.5 | 86.5% | 86.5% | 84% | 87.5% | 86.5% | 84% | 1.5 | 75.5% | 84% | 84% | 82.5% | 77% | 85.5% | 84% | 82.5% | Allentown | Education - Primary School | Allentown Education - Primary School | #N/A | #N/A | #N/A | #N/A | 3753.3368 | Allentown | Education - Primary School | Allentown Education - Primary School | #N/A | #N/A | #N/A | #N/A | 0.098597
CW Pump | 2 | 87.5% | 86.5% | 85.5% | 88.5% | 86.5% | 85.5% | 2 | 85.5% | 85.5% | 84% | 84% | 82.5% | 86.5% | 84% | 84% | Allentown | Education - Relocatable Classroom | Allentown Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 5467.3568 | Allentown | Education - Relocatable Classroom | Allentown Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 0.14933
HHWP | 3 | 88.5% | 89.5% | 85.5% | 89.5% | 89.5% | 86.5% | 3 | 86.5% | 86.5% | 86.5% | 84% | 84% | 87.5% | 87.5% | 85.5% | Allentown | Education - Secondary School | Allentown Education - Secondary School | 2721.1053 | 2742 | 2448 | 3651.4762 | 3919.6574 | Allentown | Education - Secondary School | Allentown Education - Secondary School | 0.10465 | 0.10534 | 0.10534 | 0.0030495 | 0.10569
SF | 5 | 89.5% | 89.5% | 86.5% | 89.5% | 89.5% | 88.5% | 5 | 87.5% | 87.5% | 87.5% | 85.5% | 85.5% | 87.5% | 87.5% | 87.5% | Allentown | Education - University | Allentown Education - University | 5144.8947 | 5143.4286 | 4442.5 | 4642.0952 | 6111.1765 | Allentown | Education - University | Allentown Education - University | 0.3908 | 0.39054 | 0.39054 | 0.00061183 | 0.41113
| 7.5 | 90.2% | 91% | 88.5% | 91% | 91.7% | 89.5% | 7.5 | 88.5% | 88.5% | 88.5% | 87.5% | 85.5% | 89.5% | 89.5% | 88.5% | Allentown | Grocery | Allentown Grocery | #N/A | #N/A | #N/A | #N/A | 6708.135 | Allentown | Grocery | Allentown Grocery | #N/A | #N/A | #N/A | #N/A | 0.23583
Utility | 10 | 91.7% | 91.7% | 89.5% | 91% | 91.7% | 90.2% | 10 | 89.5% | 90.2% | 89.5% | 88.5% | 88.5% | 89.5% | 89.5% | 89.5% | Allentown | Health/Medical - Hospital | Allentown Health/Medical - Hospital | 5588 | 5586.9286 | 3950.0714 | 8760 | 8760 | Allentown | Health/Medical - Hospital | Allentown Health/Medical - Hospital | 0.45754 | 0.45313 | 0.45313 | 0.092348 | 0.42914
Duquesne Light | 15 | 91.7% | 93% | 90.2% | 91.7% | 92.4% | 91% | 15 | 89.5% | 90.2% | 91% | 89.5% | 88.5% | 90.2% | 91% | 90.2% | Allentown | Health/Medical - Nursing Home | Allentown Health/Medical - Nursing Home | 3892.4737 | 3894 | 3674.7692 | 5933.7619 | 8760 | Allentown | Health/Medical - Nursing Home | Allentown Health/Medical - Nursing Home | 0.23851 | 0.2395 | 0.2395 | 0.00078703 | 0.24498
Met-Ed (FirstEnergy) | 20 | 92.4% | 93% | 91% | 91.7% | 93% | 91% | 20 | 90.2% | 91% | 91% | 90.2% | 89.5% | 90.2% | 91% | 90.2% | Allentown | Lodging - Hotel | Allentown Lodging - Hotel | 5845.3158 | 5843.6429 | 5543.7143 | 6468.619 | 8760 | Allentown | Lodging - Hotel | Allentown Lodging - Hotel | 0.60712 | 0.61294 | 0.61294 | 0.0031354 | 0.63765
Penn Power (FirstEnergy) | 25 | 93% | 93.6% | 91.7% | 93% | 93.6% | 91.7% | 25 | 90.2% | 91.7% | 91.7% | 91% | 89.5% | 91.7% | 92.4% | 91% | Allentown | Manufacturing - Bio/Tech | Allentown Manufacturing - Bio/Tech | 1735 | 1735 | 1735 | 1258 | 3570.4993 | Allentown | Manufacturing - Bio/Tech | Allentown Manufacturing - Bio/Tech | 0.53249 | 0.53461 | 0.53461 | 0 | 0.55676
PennElec (FirstEnergy) | 30 | 93.6% | 94.1% | 91.7% | 93% | 93.6% | 91.7% | 30 | 91% | 92.4% | 92.4% | 91% | 91% | 91.7% | 92.4% | 91% | Allentown | Manufacturing - Light Industrial | Allentown Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 4091.6999 | Allentown | Manufacturing - Light Industrial | Allentown Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 0.39457
West Penn Power (FirstEnergy) | 40 | 94.1% | 94.1% | 92.4% | 94.1% | 94.1% | 92.4% | 40 | 91% | 93% | 93% | 91.7% | 91% | 93% | 93% | 91.7% | Allentown | Office - Large | Allentown Office - Large | 1873.0526 | 1873.0714 | 1856.5714 | 3705.4762 | 4399.8878 | Allentown | Office - Large | Allentown Office - Large | 0.29565 | 0.29654 | 0.29654 | 0.0021115 | 0.30482
PECO | 50 | 94.1% | 94.5% | 93% | 94.1% | 94.5% | 93% | 50 | 91.7% | 93% | 93% | 92.4% | 91.7% | 93% | 93% | 92.4% | Allentown | Office - Small | Allentown Office - Small | 1705.0526 | 1705 | 1705 | 2723.4286 | 3989.5181 | Allentown | Office - Small | Allentown Office - Small | 0.27566 | 0.27749 | 0.27749 | 0 | 0.28619
PPL | 60 | 94.5% | 95% | 93.6% | 94.5% | 95% | 93.6% | 60 | 92.4% | 93.6% | 93.6% | 93% | 91.7% | 93.6% | 93.6% | 93% | Allentown | Restaurant - Fast-Food | Allentown Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 7327.8357 | Allentown | Restaurant - Fast-Food | Allentown Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 0.36077
| 75 | 94.5% | 95% | 93.6% | 94.5% | 95.4% | 93.6% | 75 | 93.6% | 93.6% | 94.1% | 93% | 93% | 93.6% | 94.1% | 93% | Allentown | Restaurant - Sit-Down | Allentown Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 5236.2084 | Allentown | Restaurant - Sit-Down | Allentown Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 0.39478
Facility Types | 100 | 95% | 95.4% | 93.6% | 95% | 95.4% | 94.1% | 100 | 93.6% | 94.1% | 94.1% | 93% | 93% | 94.1% | 94.5% | 93.6% | Allentown | Retail - Multistory Large | Allentown Retail - Multistory Large | 2957.0526 | 2957.0714 | 2888.7857 | 2676.4286 | 4892.5178 | Allentown | Retail - Multistory Large | Allentown Retail - Multistory Large | 0.45931 | 0.46061 | 0.46061 | 0 | 0.47683
Assembly | 125 | 95% | 95.4% | 94.1% | 95% | 95.4% | 95% | 125 | 93.6% | 94.1% | 94.5% | 93.6% | 93.6% | 94.1% | 94.5% | 94.5% | Allentown | Retail - Single-Story Large | Allentown Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 5485.6046 | Allentown | Retail - Single-Story Large | Allentown Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 0.49906
Education - Community College | 150 | 95.4% | 95.8% | 94.1% | 95.8% | 95.8% | 95% | 150 | 93.6% | 94.5% | 95% | 93.6% | 93.6% | 95% | 95% | 94.5% | Allentown | Retail - Small | Allentown Retail - Small | #N/A | #N/A | #N/A | #N/A | 5031.4548 | Allentown | Retail - Small | Allentown Retail - Small | #N/A | #N/A | #N/A | #N/A | 0.53305
Education - Primary School | 200 | 95.4% | 95.8% | 95% | 95.8% | 96.2% | 95.4% | 200 | 93.6% | 94.5% | 95% | 94.5% | 94.1% | 95% | 95% | 95% | Allentown | Storage - Conditioned | Allentown Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 5037.2143 | Allentown | Storage - Conditioned | Allentown Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 0.18129
Education - Relocatable Classroom | 250 | 95.4% | 95.4% | 94.5% | 95% | 95% | 95.4% | 250 | 94.5% | 95.4% | 95.4% | 94.5% | 94.5% | 95% | 95% | 95.4% | Allentown | Warehouse - Refrigerated | Allentown Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 | Allentown | Warehouse - Refrigerated | Allentown Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.50022
Education - Secondary School | 300 | 95.4% | 95.4% | 95% | 95% | 95.4% | 95.4% | 300 | N/A | 95.4% | 95.4% | 95% | N/A | 95% | 95.4% | 95.4% | Erie | Assembly | Erie Assembly | #N/A | #N/A | #N/A | #N/A | 5216.5218 | Erie | Assembly | Erie Assembly | #N/A | #N/A | #N/A | #N/A | 0.4478
Education - University | 350 | 95.4% | 95.4% | 95% | 95% | 95.4% | 95.4% | 350 | N/A | 95.4% | 95.4% | 95% | N/A | 95% | 95.4% | 95.4% | Erie | Education - Community College | Erie Education - Community College | 2560.7895 | 2560.3571 | 2344.2857 | 4941.381 | 6080.9609 | Erie | Education - Community College | Erie Education - Community College | 0.30308 | 0.30151 | 0.30151 | 0.014998 | 0.32111
Grocery | 400 | N/A | 95.4% | 95.4% | N/A | 95.4% | 95.4% | 400 | N/A | N/A | 95.4% | 95.4% | N/A | N/A | 95.4% | 95.4% | Erie | Education - Primary School | Erie Education - Primary School | #N/A | #N/A | #N/A | #N/A | 3960.9745 | Erie | Education - Primary School | Erie Education - Primary School | #N/A | #N/A | #N/A | #N/A | 0.071657
Health/Medical - Hospital | 450 | N/A | 95.8% | 95.8% | N/A | 95.4% | 95.4% | 450 | N/A | N/A | 95.8% | 95.8% | N/A | N/A | 95.4% | 95.4% | Erie | Education - Relocatable Classroom | Erie Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 5649.2985 | Erie | Education - Relocatable Classroom | Erie Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 0.11155
Health/Medical - Nursing Home | 500 | N/A | 95.8% | 95.8% | N/A | 95.8% | 95.4% | 500 | N/A | N/A | 95.8% | 95.8% | N/A | N/A | 95.8% | 95.4% | Erie | Education - Secondary School | Erie Education - Secondary School | 2174.5789 | 2178 | 2039 | 4080.3333 | 4106.0729 | Erie | Education - Secondary School | Erie Education - Secondary School | 0.088846 | 0.088311 | 0.088311 | 0.0044878 | 0.092301
Lodging - Hotel | Custom 1 | Edit | Edit | Edit | Edit | Edit | Edit | Custom 1 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Erie | Education - University | Erie Education - University | 4721.4737 | 4720.5714 | 3781.9286 | 5130.9524 | 6196.1186 | Erie | Education - University | Erie Education - University | 0.29014 | 0.28869 | 0.28869 | 0.0022772 | 0.31363
Manufacturing - Bio/Tech | Custom 2 | Edit | Edit | Edit | Edit | Edit | Edit | Custom 2 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Erie | Grocery | Erie Grocery | #N/A | #N/A | #N/A | #N/A | 6737.6792 | Erie | Grocery | Erie Grocery | #N/A | #N/A | #N/A | #N/A | 0.22324
Manufacturing - Light Industrial | Custom 3 | Edit | Edit | Edit | Edit | Edit | Edit | Custom 3 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Erie | Health/Medical - Hospital | Erie Health/Medical - Hospital | 5108.9524 | 5107.2143 | 3697.7143 | 8760 | 8760 | Erie | Health/Medical - Hospital | Erie Health/Medical - Hospital | 0.4192 | 0.41496 | 0.41496 | 0.092936 | 0.39261
Office - Large | [16 empty] | Erie | Health/Medical - Nursing Home | Erie Health/Medical - Nursing Home | 3456.3684 | 3457 | 3393.7692 | 6280.2857 | 8760 | Erie | Health/Medical - Nursing Home | Erie Health/Medical - Nursing Home | 0.22007 | 0.22 | 0.22 | 0.0016087 | 0.23254
Office - Small | [16 empty] | Erie | Lodging - Hotel | Erie Lodging - Hotel | 5198.0526 | 5196.6429 | 4765.6429 | 6829.0476 | 8760 | Erie | Lodging - Hotel | Erie Lodging - Hotel | 0.60203 | 0.60545 | 0.60545 | 0.0035124 | 0.64731
Restaurant - Fast-Food | [16 empty] | Erie | Manufacturing - Bio/Tech | Erie Manufacturing - Bio/Tech | 1448 | 1448 | 1445 | 1555 | 3615.5319 | Erie | Manufacturing - Bio/Tech | Erie Manufacturing - Bio/Tech | 0.4283 | 0.42846 | 0.42846 | 0 | 0.43925
Restaurant - Sit-Down | ESF & DSF Look Up | [15 empty] | Erie | Manufacturing - Light Industrial | Erie Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 4337.7264 | Erie | Manufacturing - Light Industrial | Erie Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 0.30772
Retail - Multistory Large | Type | Abrv | ESF | DSF | [12 empty] | Erie | Office - Large | Erie Office - Large | 1712.7895 | 1712.7143 | 1684.7857 | 4096.9524 | 4696.3734 | Erie | Office - Large | Erie Office - Large | 0.28388 | 0.284 | 0.284 | 0.0021003 | 0.29483
Retail - Single-Story Large | None | N/A | 0 | 0 | [12 empty] | Erie | Office - Small | Erie Office - Small | 1455.8947 | 1456 | 1453 | 3123.7143 | 4184.8239 | Erie | Office - Small | Erie Office - Small | 0.26144 | 0.26257 | 0.26257 | 0 | 0.27315
Retail - Small | Constant Volume | CV | 0.534 | 0.347 | [12 empty] | Erie | Restaurant - Fast-Food | Erie Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 7398.2531 | Erie | Restaurant - Fast-Food | Erie Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 0.32612
Storage - Conditioned | Air Foil/Backward Incline | AFBI | 0.354 | 0.26 | [12 empty] | Erie | Restaurant - Sit-Down | Erie Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 5332.1354 | Erie | Restaurant - Sit-Down | Erie Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 0.40627
Warehouse - Refrigerated | Air Foil/Backward Incline with Inlet Guide Vanes | AFBI IGV | 0.227 | 0.13 | [12 empty] | Erie | Retail - Multistory Large | Erie Retail - Multistory Large | 2652.6842 | 2652.9286 | 2616 | 2960.1429 | 4896.9081 | Erie | Retail - Multistory Large | Erie Retail - Multistory Large | 0.37709 | 0.37654 | 0.37654 | 0 | 0.38915
| Forward Curved | FC | 0.179 | 0.136 | [12 empty] | Erie | Retail - Single-Story Large | Erie Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 5494.447 | Erie | Retail - Single-Story Large | Erie Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 0.40257
| Forward Curved with Inlet Guide Vanes | FC IGV | 0.092 | 0.029 | [12 empty] | Erie | Retail - Small | Erie Retail - Small | #N/A | #N/A | #N/A | #N/A | 5083.2749 | Erie | Retail - Small | Erie Retail - Small | #N/A | #N/A | #N/A | #N/A | 0.52027
Program Years in Phase II | Chilled Water Pump | CHWP | 0.411 | 0.299 | [12 empty] | Erie | Storage - Conditioned | Erie Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 5222.2143 | Erie | Storage - Conditioned | Erie Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 0.12519
Program Year 7 | Heating Hot Water Pump | HHWP | 0.424 | 0 | [12 empty] | Erie | Warehouse - Refrigerated | Erie Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 | Erie | Warehouse - Refrigerated | Erie Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.47544
[17 empty] | Harrisburg | Assembly | Harrisburg Assembly | #N/A | #N/A | #N/A | #N/A | 5172.4084 | Harrisburg | Assembly | Harrisburg Assembly | #N/A | #N/A | #N/A | #N/A | 0.59999
[17 empty] | Harrisburg | Education - Community College | Harrisburg Education - Community College | 2936.9091 | 2936.5 | 2732.5 | 4150.2308 | 5771.6062 | Harrisburg | Education - Community College | Harrisburg Education - Community College | 0.42898 | 0.42586 | 0.42586 | 0.0023696 | 0.45288
[17 empty] | Harrisburg | Education - Primary School | Harrisburg Education - Primary School | #N/A | #N/A | #N/A | #N/A | 3699.1497 | Harrisburg | Education - Primary School | Harrisburg Education - Primary School | #N/A | #N/A | #N/A | #N/A | 0.15757
[17 empty] | Harrisburg | Education - Relocatable Classroom | Harrisburg Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 5375.3956 | Harrisburg | Education - Relocatable Classroom | Harrisburg Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 0.18453
Specialty Configuration Types | [16 empty] | Harrisburg | Education - Secondary School | Harrisburg Education - Secondary School | 2729.7273 | 2744 | 2539.4286 | 3491.6923 | 3865.7169 | Harrisburg | Education - Secondary School | Harrisburg Education - Secondary School | 0.17677 | 0.1783 | 0.1783 | 9.3455e-06 | 0.18475
U-Frame Motor | [16 empty] | Harrisburg | Education - University | Harrisburg Education - University | 5177.3636 | 5176 | 4470.625 | 4350.3077 | 5947.9844 | Harrisburg | Education - University | Harrisburg Education - University | 0.4012 | 0.39913 | 0.39913 | 0.00017434 | 0.42813
Design C Motor | [16 empty] | Harrisburg | Grocery | Harrisburg Grocery | #N/A | #N/A | #N/A | #N/A | 6692.2663 | Harrisburg | Grocery | Harrisburg Grocery | #N/A | #N/A | #N/A | #N/A | 0.24006
Close-Coupled Pump Motor | [16 empty] | Harrisburg | Health/Medical - Hospital | Harrisburg Health/Medical - Hospital | 5716.8462 | 5714.375 | 3687.375 | 8760 | 8760 | Harrisburg | Health/Medical - Hospital | Harrisburg Health/Medical - Hospital | 0.4974 | 0.49068 | 0.49068 | 0.09292 | 0.4533
Footless Motor | [16 empty] | Harrisburg | Health/Medical - Nursing Home | Harrisburg Health/Medical - Nursing Home | 4103.5455 | 4106 | 3724.7143 | 5823.2308 | 8760 | Harrisburg | Health/Medical - Nursing Home | Harrisburg Health/Medical - Nursing Home | 0.27674 | 0.27812 | 0.27812 | 9.9774e-05 | 0.28669
Vertical Solid Shaft Normal Thrust Motor | [16 empty] | Harrisburg | Lodging - Hotel | Harrisburg Lodging - Hotel | 6045.3636 | 6042.5 | 5568.875 | 6154.6923 | 8760 | Harrisburg | Lodging - Hotel | Harrisburg Lodging - Hotel | 0.65989 | 0.66542 | 0.66542 | 0.00044341 | 0.70617
8-Pole Motor (900 rpm) | [16 empty] | Harrisburg | Manufacturing - Bio/Tech | Harrisburg Manufacturing - Bio/Tech | 1742 | 1742 | 1737 | 1184 | 3539.4475 | Harrisburg | Manufacturing - Bio/Tech | Harrisburg Manufacturing - Bio/Tech | 0.53369 | 0.53517 | 0.53517 | 0 | 0.5662
Poly-phase Motor with Voltage < 600 Volts | [16 empty] | Harrisburg | Manufacturing - Light Industrial | Harrisburg Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 3998.3772 | Harrisburg | Manufacturing - Light Industrial | Harrisburg Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 0.49156
Other | [16 empty] | Harrisburg | Office - Large | Harrisburg Office - Large | 1912.1818 | 1911.875 | 1890.875 | 3502.6154 | 4298.3991 | Harrisburg | Office - Large | Harrisburg Office - Large | 0.36106 | 0.36205 | 0.36205 | 0 | 0.3857
[17 empty] | Harrisburg | Office - Small | Harrisburg Office - Small | 1696 | 1696 | 1693 | 2525.2308 | 3875.7055 | Harrisburg | Office - Small | Harrisburg Office - Small | 0.32858 | 0.33131 | 0.33131 | 0 | 0.35294
[17 empty] | Harrisburg | Restaurant - Fast-Food | Harrisburg Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 7300.079 | Harrisburg | Restaurant - Fast-Food | Harrisburg Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 0.38927
City | [16 empty] | Harrisburg | Restaurant - Sit-Down | Harrisburg Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 5203.0758 | Harrisburg | Restaurant - Sit-Down | Harrisburg Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 0.44848
Allentown | [16 empty] | Harrisburg | Retail - Multistory Large | Harrisburg Retail - Multistory Large | 3084.7273 | 3084.625 | 3024.75 | 2560.5385 | 4884.6329 | Harrisburg | Retail - Multistory Large | Harrisburg Retail - Multistory Large | 0.52707 | 0.52832 | 0.52832 | 0 | 0.5409
Erie | [16 empty] | Harrisburg | Retail - Single-Story Large | Harrisburg Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 5480.6702 | Harrisburg | Retail - Single-Story Large | Harrisburg Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 0.53136
Harrisburg | [16 empty] | Harrisburg | Retail - Small | Harrisburg Retail - Small | #N/A | #N/A | #N/A | #N/A | 4958.8842 | Harrisburg | Retail - Small | Harrisburg Retail - Small | #N/A | #N/A | #N/A | #N/A | 0.51018
Philadelphia | [16 empty] | Harrisburg | Storage - Conditioned | Harrisburg Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 4979.5714 | Harrisburg | Storage - Conditioned | Harrisburg Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 0.24399
Pittsburgh | [16 empty] | Harrisburg | Warehouse - Refrigerated | Harrisburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 | Harrisburg | Warehouse - Refrigerated | Harrisburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.52485
Scranton | [16 empty] | Philadelphia | Assembly | Philadelphia Assembly | #N/A | #N/A | #N/A | #N/A | 5185.9623 | Philadelphia | Assembly | Philadelphia Assembly | #N/A | #N/A | #N/A | #N/A | 0.72183
Williamsburg | [16 empty] | Philadelphia | Education - Community College | Philadelphia Education - Community College | 3306.6364 | 3306.125 | 2999.75 | 3838 | 5878.344 | Philadelphia | Education - Community College | Philadelphia Education - Community College | 0.45745 | 0.45535 | 0.45535 | 0.0015685 | 0.47594
[17 empty] | Philadelphia | Education - Primary School | Philadelphia Education - Primary School | #N/A | #N/A | #N/A | #N/A | 3894.4632 | Philadelphia | Education - Primary School | Philadelphia Education - Primary School | #N/A | #N/A | #N/A | #N/A | 0.15962
[17 empty] | Philadelphia | Education - Relocatable Classroom | Philadelphia Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 5321.4 | Philadelphia | Education - Relocatable Classroom | Philadelphia Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 0.18581
Installation Date | [16 empty] | Philadelphia | Education - Secondary School | Philadelphia Education - Secondary School | 3504.9091 | 3517 | 3346.4286 | 3341.4167 | 3936.5872 | Philadelphia | Education - Secondary School | Philadelphia Education - Secondary School | 0.17814 | 0.17926 | 0.17926 | 1.5697e-06 | 0.18553
2015-06-01 | [16 empty] | Philadelphia | Education - University | Philadelphia Education - University | 5314.2727 | 5312.125 | 5058.75 | 4189.9167 | 6053.3318 | Philadelphia | Education - University | Philadelphia Education - University | 0.42748 | 0.42607 | 0.42607 | 0 | 0.44526
2016-05-31 | [16 empty] | Philadelphia | Grocery | Philadelphia Grocery | #N/A | #N/A | #N/A | #N/A | 6668.7008 | Philadelphia | Grocery | Philadelphia Grocery | #N/A | #N/A | #N/A | #N/A | 0.26381
[17 empty] | Philadelphia | Health/Medical - Hospital | Philadelphia Health/Medical - Hospital | 6085.9167 | 6084 | 4168.125 | 8760 | 8760 | Philadelphia | Health/Medical - Hospital | Philadelphia Health/Medical - Hospital | 0.53961 | 0.53574 | 0.53574 | 0.091464 | 0.51073
[17 empty] | Philadelphia | Health/Medical - Nursing Home | Philadelphia Health/Medical - Nursing Home | 4535.2727 | 4537 | 4304 | 5477.3333 | 8760 | Philadelphia | Health/Medical - Nursing Home | Philadelphia Health/Medical - Nursing Home | 0.30084 | 0.30206 | 0.30206 | 0 | 0.31212
[17 empty] | Philadelphia | Lodging - Hotel | Philadelphia Lodging - Hotel | 6160.7273 | 6158.75 | 5885.625 | 6077 | 8760 | Philadelphia | Lodging - Hotel | Philadelphia Lodging - Hotel | 0.67186 | 0.67587 | 0.67587 | 0 | 0.71278
[17 empty] | Philadelphia | Manufacturing - Bio/Tech | Philadelphia Manufacturing - Bio/Tech | 1891 | 1891 | 1889 | 1028 | 3564.9131 | Philadelphia | Manufacturing - Bio/Tech | Philadelphia Manufacturing - Bio/Tech | 0.58152 | 0.58543 | 0.58543 | 0 | 0.60773
[17 empty] | Philadelphia | Manufacturing - Light Industrial | Philadelphia Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 4110.9041 | Philadelphia | Manufacturing - Light Industrial | Philadelphia Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 0.52403
[17 empty] | Philadelphia | Office - Large | Philadelphia Office - Large | 2173.0909 | 2173.125 | 2155.625 | 3111.5 | 4342.3132 | Philadelphia | Office - Large | Philadelphia Office - Large | 0.37291 | 0.37489 | 0.37489 | 0 | 0.39121
[17 empty] | Philadelphia | Office - Small | Philadelphia Office - Small | 1899 | 1899 | 1898 | 2267.3333 | 3784.0999 | Philadelphia | Office - Small | Philadelphia Office - Small | 0.35091 | 0.35462 | 0.35462 | 0 | 0.38412
[17 empty] | Philadelphia | Restaurant - Fast-Food | Philadelphia Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 7238.292 | Philadelphia | Restaurant - Fast-Food | Philadelphia Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 0.46864
[17 empty] | Philadelphia | Restaurant - Sit-Down | Philadelphia Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 5213.1723 | Philadelphia | Restaurant - Sit-Down | Philadelphia Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 0.52821
[17 empty] | Philadelphia | Retail - Multistory Large | Philadelphia Retail - Multistory Large | 3225.4545 | 3225.625 | 3184.875 | 2397.5 | 4885.0815 | Philadelphia | Retail - Multistory Large | Philadelphia Retail - Multistory Large | 0.53646 | 0.53809 | 0.53809 | 0 | 0.53443
[17 empty] | Philadelphia | Retail - Single-Story Large | Philadelphia Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 5497.0094 | Philadelphia | Retail - Single-Story Large | Philadelphia Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 0.62818
[17 empty] | Philadelphia | Retail - Small | Philadelphia Retail - Small | #N/A | #N/A | #N/A | #N/A | 4894.9273 | Philadelphia | Retail - Small | Philadelphia Retail - Small | #N/A | #N/A | #N/A | #N/A | 0.5312
[17 empty] | Philadelphia | Storage - Conditioned | Philadelphia Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 5168.375 | Philadelphia | Storage - Conditioned | Philadelphia Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 0.30487
[17 empty] | Philadelphia | Warehouse - Refrigerated | Philadelphia Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 | Philadelphia | Warehouse - Refrigerated | Philadelphia Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.53221
[17 empty] | Pittsburgh | Assembly | Pittsburgh Assembly | #N/A | #N/A | #N/A | #N/A | 5200.9617 | Pittsburgh | Assembly | Pittsburgh Assembly | #N/A | #N/A | #N/A | #N/A | 0.55987
[17 empty] | Pittsburgh | Education - Community College | Pittsburgh Education - Community College | 2774.8182 | 2774 | 2667.875 | 4447.0833 | 5910.9794 | Pittsburgh | Education - Community College | Pittsburgh Education - Community College | 0.40848 | 0.40628 | 0.40628 | 0.0076189 | 0.43098
[17 empty] | Pittsburgh | Education - Primary School | Pittsburgh Education - Primary School | #N/A | #N/A | #N/A | #N/A | 3789.9344 | Pittsburgh | Education - Primary School | Pittsburgh Education - Primary School | #N/A | #N/A | #N/A | #N/A | 0.17112
[17 empty] | Pittsburgh | Education - Relocatable Classroom | Pittsburgh Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 5555.7834 | Pittsburgh | Education - Relocatable Classroom | Pittsburgh Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 0.20281
[17 empty] | Pittsburgh | Education - Secondary School | Pittsburgh Education - Secondary School | 2675.6364 | 2685 | 2409.4286 | 3704.6667 | 3900.3849 | Pittsburgh | Education - Secondary School | Pittsburgh Education - Secondary School | 0.16643 | 0.16666 | 0.16666 | 0.0024877 | 0.17118
[17 empty] | Pittsburgh | Education - University | Pittsburgh Education - University | 5055.5455 | 5053.125 | 4830.375 | 4696.9167 | 6053.3801 | Pittsburgh | Education - University | Pittsburgh Education - University | 0.37908 | 0.37658 | 0.37658 | 0.0010002 | 0.40342
[17 empty] | Pittsburgh | Grocery | Pittsburgh Grocery | #N/A | #N/A | #N/A | #N/A | 6718.0022 | Pittsburgh | Grocery | Pittsburgh Grocery | #N/A | #N/A | #N/A | #N/A | 0.28713
[17 empty] | Pittsburgh | Health/Medical - Hospital | Pittsburgh Health/Medical - Hospital | 5593.25 | 5590.625 | 4093.25 | 8760 | 8760 | Pittsburgh | Health/Medical - Hospital | Pittsburgh Health/Medical - Hospital | 0.47928 | 0.47382 | 0.47382 | 0.092032 | 0.45161
[17 empty] | Pittsburgh | Health/Medical - Nursing Home | Pittsburgh Health/Medical - Nursing Home | 3899.7273 | 3902 | 3570.5714 | 5991 | 8760 | Pittsburgh | Health/Medical - Nursing Home | Pittsburgh Health/Medical - Nursing Home | 0.27624 | 0.27725 | 0.27725 | 0.00048561 | 0.28714
[17 empty] | Pittsburgh | Lodging - Hotel | Pittsburgh Lodging - Hotel | 5685.7273 | 5683 | 5238.875 | 6574.4167 | 8760 | Pittsburgh | Lodging - Hotel | Pittsburgh Lodging - Hotel | 0.6912 | 0.69554 | 0.69554 | 0.0010973 | 0.7286
[17 empty] | Pittsburgh | Manufacturing - Bio/Tech | Pittsburgh Manufacturing - Bio/Tech | 1606 | 1606 | 1602 | 1287 | 3570.7575 | Pittsburgh | Manufacturing - Bio/Tech | Pittsburgh Manufacturing - Bio/Tech | 0.54281 | 0.54414 | 0.54414 | 0 | 0.56947
[17 empty] | Pittsburgh | Manufacturing - Light Industrial | Pittsburgh Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 4167.1542 | Pittsburgh | Manufacturing - Light Industrial | Pittsburgh Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 0.41798
[17 empty] | Pittsburgh | Office - Large | Pittsburgh Office - Large | 1876.0909 | 1876.125 | 1861.625 | 3702.9167 | 4503.0835 | Pittsburgh | Office - Large | Pittsburgh Office - Large | 0.3256 | 0.32568 | 0.32568 | 0.0016757 | 0.34075
[17 empty] | Pittsburgh | Office - Small | Pittsburgh Office - Small | 1602.0909 | 1602 | 1597 | 2787.6 | 3976.4017 | Pittsburgh | Office - Small | Pittsburgh Office - Small | 0.31731 | 0.31811 | 0.31811 | 0.00022877 | 0.35114
[17 empty] | Pittsburgh | Restaurant - Fast-Food | Pittsburgh Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 7312.9629 | Pittsburgh | Restaurant - Fast-Food | Pittsburgh Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 0.44173
[17 empty] | Pittsburgh | Restaurant - Sit-Down | Pittsburgh Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 5286.3499 | Pittsburgh | Restaurant - Sit-Down | Pittsburgh Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 0.53569
[17 empty] | Pittsburgh | Retail - Multistory Large | Pittsburgh Retail - Multistory Large | 2795 | 2795 | 2756.625 | 2908.1667 | 4907.4487 | Pittsburgh | Retail - Multistory Large | Pittsburgh Retail - Multistory Large | 0.47096 | 0.47036 | 0.47036 | 0 | 0.48096
[17 empty] | Pittsburgh | Retail - Single-Story Large | Pittsburgh Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 5501.7111 | Pittsburgh | Retail - Single-Story Large | Pittsburgh Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 0.55406
[17 empty] | Pittsburgh | Retail - Small | Pittsburgh Retail - Small | #N/A | #N/A | #N/A | #N/A | 5030.3734 | Pittsburgh | Retail - Small | Pittsburgh Retail - Small | #N/A | #N/A | #N/A | #N/A | 0.58547
[17 empty] | Pittsburgh | Storage - Conditioned | Pittsburgh Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 5109.75 | Pittsburgh | Storage - Conditioned | Pittsburgh Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 0.22541
[17 empty] | Pittsburgh | Warehouse - Refrigerated | Pittsburgh Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 | Pittsburgh | Warehouse - Refrigerated | Pittsburgh Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.50754
[17 empty] | Scranton | Assembly | Scranton Assembly | #N/A | #N/A | #N/A | #N/A | 5207.0686 | Scranton | Assembly | Scranton Assembly | #N/A | #N/A | #N/A | #N/A | 0.47447
[17 empty] | Scranton | Education - Community College | Scranton Education - Community College | 2660.4545 | 2660.25 | 2429 | 4561.8462 | 5794.7066 | Scranton | Education - Community College | Scranton Education - Community College | 0.35344 | 0.35074 | 0.35074 | 0.0070821 | 0.40473
[17 empty] | Scranton | Education - Primary School | Scranton Education - Primary School | #N/A | #N/A | #N/A | #N/A | 3880.5145 | Scranton | Education - Primary School | Scranton Education - Primary School | #N/A | #N/A | #N/A | #N/A | 0.10717
[17 empty] | Scranton | Education - Relocatable Classroom | Scranton Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 5607.1097 | Scranton | Education - Relocatable Classroom | Scranton Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 0.13782
[17 empty] | Scranton | Education - Secondary School | Scranton Education - Secondary School | 2310.0909 | 2313 | 2164 | 3829.9231 | 3982.5746 | Scranton | Education - Secondary School | Scranton Education - Secondary School | 0.11768 | 0.11738 | 0.11738 | 0.0013467 | 0.12161
[17 empty] | Scranton | Education - University | Scranton Education - University | 4995.2727 | 4993.125 | 4571 | 4714 | 5956.5939 | Scranton | Education - University | Scranton Education - University | 0.31262 | 0.30957 | 0.30957 | 0 | 0.35917
[17 empty] | Scranton | Grocery | Scranton Grocery | #N/A | #N/A | #N/A | #N/A | 6724.6608 | Scranton | Grocery | Scranton Grocery | #N/A | #N/A | #N/A | #N/A | 0.21381
[17 empty] | Scranton | Health/Medical - Hospital | Scranton Health/Medical - Hospital | 5266 | 5263.25 | 3713.25 | 8760 | 8760 | Scranton | Health/Medical - Hospital | Scranton Health/Medical - Hospital | 0.44428 | 0.4359 | 0.4359 | 0.090208 | 0.39803
[17 empty] | Scranton | Health/Medical - Nursing Home | Scranton Health/Medical - Nursing Home | 3709.6364 | 3711 | 3687 | 6222.6154 | 8760 | Scranton | Health/Medical - Nursing Home | Scranton Health/Medical - Nursing Home | 0.22911 | 0.22909 | 0.22909 | 0 | 0.25236
[17 empty] | Scranton | Lodging - Hotel | Scranton Lodging - Hotel | 5654.5455 | 5651.75 | 5352.5 | 6628.2308 | 8760 | Scranton | Lodging - Hotel | Scranton Lodging - Hotel | 0.58598 | 0.5875 | 0.5875 | 0.00087673 | 0.64615
[17 empty] | Scranton | Manufacturing - Bio/Tech | Scranton Manufacturing - Bio/Tech | 1558 | 1558 | 1558 | 1393 | 3551.6865 | Scranton | Manufacturing - Bio/Tech | Scranton Manufacturing - Bio/Tech | 0.47654 | 0.47622 | 0.47622 | 0 | 0.50289
[17 empty] | Scranton | Manufacturing - Light Industrial | Scranton Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 4251.0891 | Scranton | Manufacturing - Light Industrial | Scranton Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 0.36457
[17 empty] | Scranton | Office - Large | Scranton Office - Large | 1740.8182 | 1740.75 | 1728.125 | 3808.75 | 4440.9018 | Scranton | Office - Large | Scranton Office - Large | 0.29514 | 0.2955 | 0.2955 | 0.00031638 | 0.33526
[17 empty] | Scranton | Office - Small | Scranton Office - Small | 1534 | 1534 | 1533 | 2862.6923 | 4013.6553 | Scranton | Office - Small | Scranton Office - Small | 0.28103 | 0.2823 | 0.2823 | 0 | 0.3023
[17 empty] | Scranton | Restaurant - Fast-Food | Scranton Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 7342.3556 | Scranton | Restaurant - Fast-Food | Scranton Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 0.37814
[17 empty] | Scranton | Restaurant - Sit-Down | Scranton Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 5288.3704 | Scranton | Restaurant - Sit-Down | Scranton Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 0.3991
[17 empty] | Scranton | Retail - Multistory Large | Scranton Retail - Multistory Large | 2735.3636 | 2735.5 | 2702.125 | 2841 | 4889.7202 | Scranton | Retail - Multistory Large | Scranton Retail - Multistory Large | 0.42164 | 0.4206 | 0.4206 | 0 | 0.44446
[17 empty] | Scranton | Retail - Single-Story Large | Scranton Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 5492.5804 | Scranton | Retail - Single-Story Large | Scranton Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 0.47322
[17 empty] | Scranton | Retail - Small | Scranton Retail - Small | #N/A | #N/A | #N/A | #N/A | 5062.8699 | Scranton | Retail - Small | Scranton Retail - Small | #N/A | #N/A | #N/A | #N/A | 0.45129
[17 empty] | Scranton | Storage - Conditioned | Scranton Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 5187.875 | Scranton | Storage - Conditioned | Scranton Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 0.14719
[17 empty] | Scranton | Warehouse - Refrigerated | Scranton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 | Scranton | Warehouse - Refrigerated | Scranton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.48286
[17 empty] | Williamsburg | Assembly | Williamsburg Assembly | #N/A | #N/A | #N/A | #N/A | 5183.9215 | Williamsburg | Assembly | Williamsburg Assembly | #N/A | #N/A | #N/A | #N/A | 0.52478
[17 empty] | Williamsburg | Education - Community College | Williamsburg Education - Community College | 2726.9091 | 2726.5 | 2529.75 | 4408 | 5824.1947 | Williamsburg | Education - Community College | Williamsburg Education - Community College | 0.42619 | 0.42338 | 0.42338 | 0.0064528 | 0.46671
[17 empty] | Williamsburg | Education - Primary School | Williamsburg Education - Primary School | #N/A | #N/A | #N/A | #N/A | 3762.6192 | Williamsburg | Education - Primary School | Williamsburg Education - Primary School | #N/A | #N/A | #N/A | #N/A | 0.12443
[17 empty] | Williamsburg | Education - Relocatable Classroom | Williamsburg Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 5439.2499 | Williamsburg | Education - Relocatable Classroom | Williamsburg Education - Relocatable Classroom | #N/A | #N/A | #N/A | #N/A | 0.14639
[17 empty] | Williamsburg | Education - Secondary School | Williamsburg Education - Secondary School | 2572.9091 | 2604 | 2423 | 3657.6923 | 3928.465 | Williamsburg | Education - Secondary School | Williamsburg Education - Secondary School | 0.16424 | 0.16507 | 0.16507 | 0 | 0.16521
[17 empty] | Williamsburg | Education - University | Williamsburg Education - University | 5016.3636 | 5014.625 | 4448.125 | 4565.9231 | 5985.1304 | Williamsburg | Education - University | Williamsburg Education - University | 0.36218 | 0.35907 | 0.35907 | 0.00077118 | 0.39892
[17 empty] | Williamsburg | Grocery | Williamsburg Grocery | #N/A | #N/A | #N/A | #N/A | 6710.4693 | Williamsburg | Grocery | Williamsburg Grocery | #N/A | #N/A | #N/A | #N/A | 0.24154
[17 empty] | Williamsburg | Health/Medical - Hospital | Williamsburg Health/Medical - Hospital | 5628.2308 | 5625.625 | 3670.25 | 8760 | 8760 | Williamsburg | Health/Medical - Hospital | Williamsburg Health/Medical - Hospital | 0.46512 | 0.45976 | 0.45976 | 0.092272 | 0.41429
[17 empty] | Williamsburg | Health/Medical - Nursing Home | Williamsburg Health/Medical - Nursing Home | 3817.8182 | 3819 | 3722 | 6044.9231 | 8760 | Williamsburg | Health/Medical - Nursing Home | Williamsburg Health/Medical - Nursing Home | 0.26204 | 0.26261 | 0.26261 | 0.00099699 | 0.27504
[17 empty] | Williamsburg | Lodging - Hotel | Williamsburg Lodging - Hotel | 5775.6364 | 5772.875 | 5327.75 | 6387.2308 | 8760 | Williamsburg | Lodging - Hotel | Williamsburg Lodging - Hotel | 0.65628 | 0.65924 | 0.65924 | 0.0014831 | 0.7092
[17 empty] | Williamsburg | Manufacturing - Bio/Tech | Williamsburg Manufacturing - Bio/Tech | 1633 | 1633 | 1632 | 1277 | 3572.697 | Williamsburg | Manufacturing - Bio/Tech | Williamsburg Manufacturing - Bio/Tech | 0.50084 | 0.50124 | 0.50124 | 0 | 0.52132
[17 empty] | Williamsburg | Manufacturing - Light Industrial | Williamsburg Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 4083.5705 | Williamsburg | Manufacturing - Light Industrial | Williamsburg Manufacturing - Light Industrial | #N/A | #N/A | #N/A | #N/A | 0.40104
[17 empty] | Williamsburg | Office - Large | Williamsburg Office - Large | 1814.7273 | 1814.625 | 1797.75 | 3651.7692 | 4352.8066 | Williamsburg | Office - Large | Williamsburg Office - Large | 0.32725 | 0.32719 | 0.32719 | 0.0014034 | 0.34729
[17 empty] | Williamsburg | Office - Small | Williamsburg Office - Small | 1606 | 1606 | 1606 | 2684.7692 | 3924.1665 | Williamsburg | Office - Small | Williamsburg Office - Small | 0.30788 | 0.30938 | 0.30938 | 0 | 0.32867
[17 empty] | Williamsburg | Restaurant - Fast-Food | Williamsburg Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 7331.6491 | Williamsburg | Restaurant - Fast-Food | Williamsburg Restaurant - Fast-Food | #N/A | #N/A | #N/A | #N/A | 0.41502
[17 empty] | Williamsburg | Restaurant - Sit-Down | Williamsburg Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 5239.1261 | Williamsburg | Restaurant - Sit-Down | Williamsburg Restaurant - Sit-Down | #N/A | #N/A | #N/A | #N/A | 0.48261
[17 empty] | Williamsburg | Retail - Multistory Large | Williamsburg Retail - Multistory Large | 2898.1818 | 2897.875 | 2847.375 | 2659.6154 | 4895.7917 | Williamsburg | Retail - Multistory Large | Williamsburg Retail - Multistory Large | 0.4706 | 0.46947 | 0.46947 | 0 | 0.48526
[17 empty] | Williamsburg | Retail - Single-Story Large | Williamsburg Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 5487.217 | Williamsburg | Retail - Single-Story Large | Williamsburg Retail - Single-Story Large | #N/A | #N/A | #N/A | #N/A | 0.46643
[17 empty] | Williamsburg | Retail - Small | Williamsburg Retail - Small | #N/A | #N/A | #N/A | #N/A | 5017.9805 | Williamsburg | Retail - Small | Williamsburg Retail - Small | #N/A | #N/A | #N/A | #N/A | 0.49987
[17 empty] | Williamsburg | Storage - Conditioned | Williamsburg Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 5027.5 | Williamsburg | Storage - Conditioned | Williamsburg Storage - Conditioned | #N/A | #N/A | #N/A | #N/A | 0.19887
[17 empty] | Williamsburg | Warehouse - Refrigerated | Williamsburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 | Williamsburg | Warehouse - Refrigerated | Williamsburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.51293
[18 empty] | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg |  | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
[17 empty] | Assembly | 5187.8264 | 5216.5218 | 5172.4084 | 5185.9623 | 5200.9617 | 5207.0686 | 5183.9215 | Assembly | 0.52664 | 0.4478 | 0.59999 | 0.72183 | 0.55987 | 0.47447 | 0.52478
[17 empty] | Education - Community College | 5972.4949 | 6080.9609 | 5771.6062 | 5878.344 | 5910.9794 | 5794.7066 | 5824.1947 | Education - Community College | 0.43972 | 0.32111 | 0.45288 | 0.47594 | 0.43098 | 0.40473 | 0.46671
[17 empty] | Education - Primary School | 3753.3368 | 3960.9745 | 3699.1497 | 3894.4632 | 3789.9344 | 3880.5145 | 3762.6192 | Education - Primary School | 0.098597 | 0.071657 | 0.15757 | 0.15962 | 0.17112 | 0.10717 | 0.12443
[17 empty] | Education - Relocatable Classroom | 5467.3568 | 5649.2985 | 5375.3956 | 5321.4 | 5555.7834 | 5607.1097 | 5439.2499 | Education - Relocatable Classroom | 0.14933 | 0.11155 | 0.18453 | 0.18581 | 0.20281 | 0.13782 | 0.14639
[17 empty] | Education - Secondary School | 3919.6574 | 4106.0729 | 3865.7169 | 3936.5872 | 3900.3849 | 3982.5746 | 3928.465 | Education - Secondary School | 0.10569 | 0.092301 | 0.18475 | 0.18553 | 0.17118 | 0.12161 | 0.16521
[17 empty] | Education - University | 6111.1765 | 6196.1186 | 5947.9844 | 6053.3318 | 6053.3801 | 5956.5939 | 5985.1304 | Education - University | 0.41113 | 0.31363 | 0.42813 | 0.44526 | 0.40342 | 0.35917 | 0.39892
[17 empty] | Grocery | 6708.135 | 6737.6792 | 6692.2663 | 6668.7008 | 6718.0022 | 6724.6608 | 6710.4693 | Grocery | 0.23583 | 0.22324 | 0.24006 | 0.26381 | 0.28713 | 0.21381 | 0.24154
[17 empty] | Health/Medical - Hospital | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health/Medical - Hospital | 0.42914 | 0.39261 | 0.4533 | 0.51073 | 0.45161 | 0.39803 | 0.41429
[17 empty] | Health/Medical - Nursing Home | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health/Medical - Nursing Home | 0.24498 | 0.23254 | 0.28669 | 0.31212 | 0.28714 | 0.25236 | 0.27504
[17 empty] | Lodging - Hotel | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Lodging - Hotel | 0.63765 | 0.64731 | 0.70617 | 0.71278 | 0.7286 | 0.64615 | 0.7092
[17 empty] | Manufacturing - Bio/Tech | 3570.4993 | 3615.5319 | 3539.4475 | 3564.9131 | 3570.7575 | 3551.6865 | 3572.697 | Manufacturing - Bio/Tech | 0.55676 | 0.43925 | 0.5662 | 0.60773 | 0.56947 | 0.50289 | 0.52132
[17 empty] | Manufacturing - Light Industrial | 4091.6999 | 4337.7264 | 3998.3772 | 4110.9041 | 4167.1542 | 4251.0891 | 4083.5705 | Manufacturing - Light Industrial | 0.39457 | 0.30772 | 0.49156 | 0.52403 | 0.41798 | 0.36457 | 0.40104
[17 empty] | Office - Large | 4399.8878 | 4696.3734 | 4298.3991 | 4342.3132 | 4503.0835 | 4440.9018 | 4352.8066 | Office - Large | 0.30482 | 0.29483 | 0.3857 | 0.39121 | 0.34075 | 0.33526 | 0.34729
[17 empty] | Office - Small | 3989.5181 | 4184.8239 | 3875.7055 | 3784.0999 | 3976.4017 | 4013.6553 | 3924.1665 | Office - Small | 0.28619 | 0.27315 | 0.35294 | 0.38412 | 0.35114 | 0.3023 | 0.32867
[17 empty] | Restaurant - Fast-Food | 7327.8357 | 7398.2531 | 7300.079 | 7238.292 | 7312.9629 | 7342.3556 | 7331.6491 | Restaurant - Fast-Food | 0.36077 | 0.32612 | 0.38927 | 0.46864 | 0.44173 | 0.37814 | 0.41502
[17 empty] | Restaurant - Sit-Down | 5236.2084 | 5332.1354 | 5203.0758 | 5213.1723 | 5286.3499 | 5288.3704 | 5239.1261 | Restaurant - Sit-Down | 0.39478 | 0.40627 | 0.44848 | 0.52821 | 0.53569 | 0.3991 | 0.48261
[17 empty] | Retail - Multistory Large | 4892.5178 | 4896.9081 | 4884.6329 | 4885.0815 | 4907.4487 | 4889.7202 | 4895.7917 | Retail - Multistory Large | 0.47683 | 0.38915 | 0.5409 | 0.53443 | 0.48096 | 0.44446 | 0.48526
[17 empty] | Retail - Single-Story Large | 5485.6046 | 5494.447 | 5480.6702 | 5497.0094 | 5501.7111 | 5492.5804 | 5487.217 | Retail - Single-Story Large | 0.49906 | 0.40257 | 0.53136 | 0.62818 | 0.55406 | 0.47322 | 0.46643
[17 empty] | Retail - Small | 5031.4548 | 5083.2749 | 4958.8842 | 4894.9273 | 5030.3734 | 5062.8699 | 5017.9805 | Retail - Small | 0.53305 | 0.52027 | 0.51018 | 0.5312 | 0.58547 | 0.45129 | 0.49987
[17 empty] | Storage - Conditioned | 5037.2143 | 5222.2143 | 4979.5714 | 5168.375 | 5109.75 | 5187.875 | 5027.5 | Storage - Conditioned | 0.18129 | 0.12519 | 0.24399 | 0.30487 | 0.22541 | 0.14719 | 0.19887
[17 empty] | Warehouse - Refrigerated | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | Warehouse - Refrigerated | 0.50022 | 0.47544 | 0.52485 | 0.53221 | 0.50754 | 0.48286 | 0.51293
[17 empty] | CHW Pump | [7 empty] | CHW Pump
[17 empty] | Facility Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
[17 empty] | Education - Community College | 2868.1579 | 2560.7895 | 2936.9091 | 3306.6364 | 2774.8182 | 2660.4545 | 2726.9091 | Education - Community College | 0.42302 | 0.30308 | 0.42898 | 0.45745 | 0.40848 | 0.35344 | 0.42619
[17 empty] | Education - Secondary School | 2721.1053 | 2174.5789 | 2729.7273 | 3504.9091 | 2675.6364 | 2310.0909 | 2572.9091 | Education - Secondary School | 0.10465 | 0.088846 | 0.17677 | 0.17814 | 0.16643 | 0.11768 | 0.16424
[17 empty] | Education - University | 5144.8947 | 4721.4737 | 5177.3636 | 5314.2727 | 5055.5455 | 4995.2727 | 5016.3636 | Education - University | 0.3908 | 0.29014 | 0.4012 | 0.42748 | 0.37908 | 0.31262 | 0.36218
[17 empty] | Health/Medical - Hospital | 5588 | 5108.9524 | 5716.8462 | 6085.9167 | 5593.25 | 5266 | 5628.2308 | Health/Medical - Hospital | 0.45754 | 0.4192 | 0.4974 | 0.53961 | 0.47928 | 0.44428 | 0.46512
[17 empty] | Health/Medical - Nursing Home | 3892.4737 | 3456.3684 | 4103.5455 | 4535.2727 | 3899.7273 | 3709.6364 | 3817.8182 | Health/Medical - Nursing Home | 0.23851 | 0.22007 | 0.27674 | 0.30084 | 0.27624 | 0.22911 | 0.26204
[17 empty] | Lodging - Hotel | 5845.3158 | 5198.0526 | 6045.3636 | 6160.7273 | 5685.7273 | 5654.5455 | 5775.6364 | Lodging - Hotel | 0.60712 | 0.60203 | 0.65989 | 0.67186 | 0.6912 | 0.58598 | 0.65628
[17 empty] | Manufacturing - Bio/Tech | 1735 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633 | Manufacturing - Bio/Tech | 0.53249 | 0.4283 | 0.53369 | 0.58152 | 0.54281 | 0.47654 | 0.50084
[17 empty] | Office - Large | 1873.0526 | 1712.7895 | 1912.1818 | 2173.0909 | 1876.0909 | 1740.8182 | 1814.7273 | Office - Large | 0.29565 | 0.28388 | 0.36106 | 0.37291 | 0.3256 | 0.29514 | 0.32725
[17 empty] | Office - Small | 1705.0526 | 1455.8947 | 1696 | 1899 | 1602.0909 | 1534 | 1606 | Office - Small | 0.27566 | 0.26144 | 0.32858 | 0.35091 | 0.31731 | 0.28103 | 0.30788
[17 empty] | Retail - Multistory Large | 2957.0526 | 2652.6842 | 3084.7273 | 3225.4545 | 2795 | 2735.3636 | 2898.1818 | Retail - Multistory Large | 0.45931 | 0.37709 | 0.52707 | 0.53646 | 0.47096 | 0.42164 | 0.4706
[17 empty] | CT Fan | [7 empty] | CT Fan
[17 empty] | Facility Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
[17 empty] | Education - Community College | 2867.8571 | 2560.3571 | 2936.5 | 3306.125 | 2774 | 2660.25 | 2726.5 | Education - Community College | 0.4231 | 0.30151 | 0.42586 | 0.45535 | 0.40628 | 0.35074 | 0.42338
[17 empty] | Education - Secondary School | 2742 | 2178 | 2744 | 3517 | 2685 | 2313 | 2604 | Education - Secondary School | 0.10534 | 0.088311 | 0.1783 | 0.17926 | 0.16666 | 0.11738 | 0.16507
[17 empty] | Education - University | 5143.4286 | 4720.5714 | 5176 | 5312.125 | 5053.125 | 4993.125 | 5014.625 | Education - University | 0.39054 | 0.28869 | 0.39913 | 0.42607 | 0.37658 | 0.30957 | 0.35907
[17 empty] | Health/Medical - Hospital | 5586.9286 | 5107.2143 | 5714.375 | 6084 | 5590.625 | 5263.25 | 5625.625 | Health/Medical - Hospital | 0.45313 | 0.41496 | 0.49068 | 0.53574 | 0.47382 | 0.4359 | 0.45976
[17 empty] | Health/Medical - Nursing Home | 3894 | 3457 | 4106 | 4537 | 3902 | 3711 | 3819 | Health/Medical - Nursing Home | 0.2395 | 0.22 | 0.27812 | 0.30206 | 0.27725 | 0.22909 | 0.26261
[17 empty] | Lodging - Hotel | 5843.6429 | 5196.6429 | 6042.5 | 6158.75 | 5683 | 5651.75 | 5772.875 | Lodging - Hotel | 0.61294 | 0.60545 | 0.66542 | 0.67587 | 0.69554 | 0.5875 | 0.65924
[17 empty] | Manufacturing - Bio/Tech | 1735 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633 | Manufacturing - Bio/Tech | 0.53461 | 0.42846 | 0.53517 | 0.58543 | 0.54414 | 0.47622 | 0.50124
[17 empty] | Office - Large | 1873.0714 | 1712.7143 | 1911.875 | 2173.125 | 1876.125 | 1740.75 | 1814.625 | Office - Large | 0.29654 | 0.284 | 0.36205 | 0.37489 | 0.32568 | 0.2955 | 0.32719
[17 empty] | Office - Small | 1705 | 1456 | 1696 | 1899 | 1602 | 1534 | 1606 | Office - Small | 0.27749 | 0.26257 | 0.33131 | 0.35462 | 0.31811 | 0.2823 | 0.30938
[17 empty] | Retail - Multistory Large | 2957.0714 | 2652.9286 | 3084.625 | 3225.625 | 2795 | 2735.5 | 2897.875 | Retail - Multistory Large | 0.46061 | 0.37654 | 0.52832 | 0.53809 | 0.47036 | 0.4206 | 0.46947
[17 empty] | HHW Pump | [7 empty] | HHW Pump
[17 empty] | Facility Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
[17 empty] | Education - Community College | 4453.8571 | 4941.381 | 4150.2308 | 3838 | 4447.0833 | 4561.8462 | 4408 | Education - Community College | 0.010634 | 0.014998 | 0.0023696 | 0.0015685 | 0.0076189 | 0.0070821 | 0.0064528
[17 empty] | Education - Secondary School | 3651.4762 | 4080.3333 | 3491.6923 | 3341.4167 | 3704.6667 | 3829.9231 | 3657.6923 | Education - Secondary School | 0.0030495 | 0.0044878 | 9.3455e-06 | 1.5697e-06 | 0.0024877 | 0.0013467 | 0
[17 empty] | Education - University | 4642.0952 | 5130.9524 | 4350.3077 | 4189.9167 | 4696.9167 | 4714 | 4565.9231 | Education - University | 0.00061183 | 0.0022772 | 0.00017434 | 0 | 0.0010002 | 0 | 0.00077118
[17 empty] | Health/Medical - Hospital | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health/Medical - Hospital | 0.092348 | 0.092936 | 0.09292 | 0.091464 | 0.092032 | 0.090208 | 0.092272
[17 empty] | Health/Medical - Nursing Home | 5933.7619 | 6280.2857 | 5823.2308 | 5477.3333 | 5991 | 6222.6154 | 6044.9231 | Health/Medical - Nursing Home | 0.00078703 | 0.0016087 | 9.9774e-05 | 0 | 0.00048561 | 0 | 0.00099699
[17 empty] | Lodging - Hotel | 6468.619 | 6829.0476 | 6154.6923 | 6077 | 6574.4167 | 6628.2308 | 6387.2308 | Lodging - Hotel | 0.0031354 | 0.0035124 | 0.00044341 | 0 | 0.0010973 | 0.00087673 | 0.0014831
[17 empty] | Manufacturing - Bio/Tech | 1258 | 1555 | 1184 | 1028 | 1287 | 1393 | 1277 | Manufacturing - Bio/Tech | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | Office - Large | 3705.4762 | 4096.9524 | 3502.6154 | 3111.5 | 3702.9167 | 3808.75 | 3651.7692 | Office - Large | 0.0021115 | 0.0021003 | 0 | 0 | 0.0016757 | 0.00031638 | 0.0014034
[17 empty] | Office - Small | 2723.4286 | 3123.7143 | 2525.2308 | 2267.3333 | 2787.6 | 2862.6923 | 2684.7692 | Office - Small | 0 | 0 | 0 | 0 | 0.00022877 | 0 | 0
[17 empty] | Retail - Multistory Large | 2676.4286 | 2960.1429 | 2560.5385 | 2397.5 | 2908.1667 | 2841 | 2659.6154 | Retail - Multistory Large | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | Chiller 1 CW Pump | [7 empty] | Chiller 1 CW Pump
[17 empty] | Facility Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
[17 empty] | Education - Community College | 2611.4286 | 2344.2857 | 2732.5 | 2999.75 | 2667.875 | 2429 | 2529.75 | Education - Community College | 0.4231 | 0.30151 | 0.42586 | 0.45535 | 0.40628 | 0.35074 | 0.42338
[17 empty] | Education - Secondary School | 2448 | 2039 | 2539.4286 | 3346.4286 | 2409.4286 | 2164 | 2423 | Education - Secondary School | 0.10534 | 0.088311 | 0.1783 | 0.17926 | 0.16666 | 0.11738 | 0.16507
[17 empty] | Education - University | 4442.5 | 3781.9286 | 4470.625 | 5058.75 | 4830.375 | 4571 | 4448.125 | Education - University | 0.39054 | 0.28869 | 0.39913 | 0.42607 | 0.37658 | 0.30957 | 0.35907
[17 empty] | Health/Medical - Hospital | 3950.0714 | 3697.7143 | 3687.375 | 4168.125 | 4093.25 | 3713.25 | 3670.25 | Health/Medical - Hospital | 0.45313 | 0.41496 | 0.49068 | 0.53574 | 0.47382 | 0.4359 | 0.45976
[17 empty] | Health/Medical - Nursing Home | 3674.7692 | 3393.7692 | 3724.7143 | 4304 | 3570.5714 | 3687 | 3722 | Health/Medical - Nursing Home | 0.2395 | 0.22 | 0.27812 | 0.30206 | 0.27725 | 0.22909 | 0.26261
[17 empty] | Lodging - Hotel | 5543.7143 | 4765.6429 | 5568.875 | 5885.625 | 5238.875 | 5352.5 | 5327.75 | Lodging - Hotel | 0.61294 | 0.60545 | 0.66542 | 0.67587 | 0.69554 | 0.5875 | 0.65924
[17 empty] | Manufacturing - Bio/Tech | 1735 | 1445 | 1737 | 1889 | 1602 | 1558 | 1632 | Manufacturing - Bio/Tech | 0.53461 | 0.42846 | 0.53517 | 0.58543 | 0.54414 | 0.47622 | 0.50124
[17 empty] | Office - Large | 1856.5714 | 1684.7857 | 1890.875 | 2155.625 | 1861.625 | 1728.125 | 1797.75 | Office - Large | 0.29654 | 0.284 | 0.36205 | 0.37489 | 0.32568 | 0.2955 | 0.32719
[17 empty] | Office - Small | 1705 | 1453 | 1693 | 1898 | 1597 | 1533 | 1606 | Office - Small | 0.27749 | 0.26257 | 0.33131 | 0.35462 | 0.31811 | 0.2823 | 0.30938
[17 empty] | Retail - Multistory Large | 2888.7857 | 2616 | 3024.75 | 3184.875 | 2756.625 | 2702.125 | 2847.375 | Retail - Multistory Large | 0.46061 | 0.37654 | 0.52832 | 0.53809 | 0.47036 | 0.4206 | 0.46947